## Sheet1
Package ID | Strategy ID | Functional Location | Action ID | Description | Interval | Interval Units | Recommended Resource | Shutdown Required | Reference Column | Job Plan | Action Basis
Gidgealpa Gas Satellite - Buildings - Buildings | GIDG BLD 1010-CHG-001 | 1010-CHG-001 | Motor Control Centre-GIDG_A07 | Inspect the condition of the BCM wiring for damage or deterioration | 1 | Y | 01 | 00 |  |  | 2250715.docx
Gidgealpa Gas Satellite - Buildings - Buildings | GIDG BLD 1010-PLC-002 | 1010-PLC-002 | PLC Battery- GIDG_A01 | Change out PLC Battery | 3 | Y | 01 | 00 |  |  | REPLACE-PM-CL.LC-003628-C-0002.docx
Gidgealpa Gas Satellite - Buildings - Buildings | GIDG BLD 1010-PLC-001 | 1010-PLC-001 | PLC Battery- GIDG_A01 | Change out PLC Battery | 3 | Y | 01 | 00 |  |  | REPLACE-PM-CL.LC-003628-C-0002.docx
Gidgealpa Gas Satellite - Buildings - Buildings | GIDG BLD 1010-CHG-001 | 1010-CHG-001 | Motor Control Centre-GIDG_A06 | Inspect the batteries for signs of swelling / distortion or other effects from excess heat | 1 | Y | 01 | 00 |  |  | 2250715.docx
Gidgealpa Gas Satellite - Buildings - Buildings | GIDG BLD 1010-CHG-001 | 1010-CHG-001 | Motor Control Centre-GIDG_A05 | Remove dust buildup from the battery casings and terminals | 1 | Y | 01 | 00 |  |  | 2250715.docx
Gidgealpa Gas Satellite - Buildings - Buildings | GIDG BLD 1010-CHG-001 | 1010-CHG-001 | Motor Control Centre-GIDG_A09 | Test SMR and alarms | 1 | Y | 01 | 00 |  |  | 2250715.docx
Gidgealpa Gas Satellite - Buildings - Buildings | GIDG BLD 1010-CHG-001 | 1010-CHG-001 | Motor Control Centre-GIDG_A01 | Check indicator lights on 24 volt supply UPS in MCC to confirm they are healthy | 1 | W | 44 | 01 | 1010-CHG-001 1W-44-01- |  | OEC Tasks List
Gidgealpa Gas Satellite - Buildings - Buildings | GIDG BLD 1010-CHG-001 | 1010-CHG-001 | Motor Control Centre-GIDG_A02 | Complete lamp test on ESD panel | 1 | W | 44 | 01 | 1010-CHG-001 1W-44-01- |  | OEC Tasks List
Gidgealpa Gas Satellite - Buildings - Buildings | GIDG BLD 1010-CHG-001 | 1010-CHG-001 | Motor Control Centre-GIDG_A03 | Clean all dust from the rectifier enclosure | 1 | Y | 01 | 00 |  |  | 2250715.docx
Gidgealpa Gas Satellite - Buildings - Buildings | GIDG BLD 1010-CHG-001 | 1010-CHG-001 | Motor Control Centre-GIDG_A04 | Inspect the SMR internals for excessive amounts of dust | 1 | Y | 01 | 00 |  |  | 2250715.docx
Gidgealpa Gas Satellite - Buildings - Buildings | GIDG BLD 1010-CHG-001 | 1010-CHG-001 | Motor Control Centre-GIDG_A08 | Test Battery Cell Condition | 1 | Y | 01 | 00 |  |  | 2250715.docx
Gidgealpa Gas Satellite - Buildings - Buildings | GIDG BLD 1010-PLC-003 | 1010-PLC-003 | PLC Battery- GIDG_A01 | Change out PLC Battery | 3 | Y | 01 | 00 |  |  | REPLACE-PM-CL.LC-003628-C-0002.docx
Gidgealpa Gas Satellite - Compression - Compressor Building | GIDG COMP 1010-CR-053 | 1010-CR-053 | Crane-Gantry-GIDG_A04 | Check the devices and equipment | 1 | Y | 21 | 00 |  |  | 2218899.docx
Gidgealpa Gas Satellite - Compression - Compressor Building | GIDG COMP 1010-CR-053 | 1010-CR-053 | Crane-Gantry-GIDG_A01 | Isolate all motive power to the crane | 1 | Y | 21 | 00 |  |  | 2218899.docx
Gidgealpa Gas Satellite - Compression - Compressor Building | GIDG COMP 1010-CR-053 | 1010-CR-053 | Crane-Gantry-GIDG_A03 | Check as per attached sheet record | 1 | Y | 21 | 00 |  |  | 2218899.docx
Gidgealpa Gas Satellite - Compression - Compressor Building | GIDG COMP 1010-CR-053 | 1010-CR-053 | Crane-Gantry-GIDG_A05 | Ensure all isolations have been returned to there original settings | 1 | Y | 21 | 00 |  |  | 2218899.docx
Gidgealpa Gas Satellite - Compression - Compressor Building | GIDG COMP 1010-CR-053 | 1010-CR-053 | Crane-Gantry-GIDG_A02 | Ensure all electrical isolations are carried out before working on the crane electrics | 1 | Y | 21 | 00 |  |  | 2218899.docx
Gidgealpa Gas Satellite - Compression - Compressor Package 3 | GIDG COMP 1010-E-002 | 1010-E-002 | Cooler-Compressor-GIDG_A02 | Remove belt guard to access belts | 1 | Y | 4 | 00 |  |  | 2223330.docx
Gidgealpa Gas Satellite - Compression - Compressor Package 3 | GIDG COMP 1010-KX-003 | 1010-KX-003 | Compressor Package IE-Gas Superior SW66-GIDG_A016 | Inspection & Calibration Check Task Compressor / Engine Package Vibration Switches | 1 | Y | 01 | 00 |  |  | 1010-295-TIN-0003.pdf
Gidgealpa Gas Satellite - Compression - Compressor Package 3 | GIDG COMP 1010-KX-003 | 1010-KX-003 | Compressor Package IE-Gas Superior SW66-GIDG_A03 | Service & Calibration Task Engine / Compressor Lube Oil Pressure Switch | 1 | Y | 01 | 00 |  |  | 1010-295-TIN-0003.pdf
Gidgealpa Gas Satellite - Compression - Compressor Package 3 | GIDG COMP 1010-KX-003 | 1010-KX-003 | Compressor Package IE-Gas Superior SW66-GIDG_A010 | Inspection & Calibration Check Compressor Inlet Valve Differential Pressure Transmitter | 1 | Y | 01 | 00 |  |  | 1010-295-TIN-0003.pdf
Gidgealpa Gas Satellite - Compression - Compressor Package 3 | GIDG COMP 1010-KX-003 | 1010-KX-003 | Compressor Package IE-Gas Superior SW66-GIDG_A018 | Service & Calibration Task Compressor Recycle Valve & Positioner | 1 | Y | 01 | 00 |  |  | 1010-295-TIN-0003.pdf
Gidgealpa Gas Satellite - Compression - Compressor Package 3 | GIDG COMP 1010-KX-003 | 1010-KX-003 | Compressor Package IE-Gas Superior SW66-GIDG_A02 | Inspection & Calibration Check Scrubber Suction / Lube Oil Cooler / Air Manifold Temperature RTD | 1 | Y | 01 | 00 |  |  | 1010-295-TIN-0003.pdf
Gidgealpa Gas Satellite - Compression - Compressor Package 3 | GIDG COMP 1010-KX-003 | 1010-KX-003 | Compressor Package IE-Gas Superior SW66-GIDG_A08 | Inspection & Function Check Task Compressor / Engine Cooling Water Flow Switches | 1 | Y | 01 | 00 |  |  | 1010-295-TIN-0003.pdf
Gidgealpa Gas Satellite - Compression - Compressor Package 3 | GIDG COMP 1010-KX-003 | 1010-KX-003 | Compressor Package IE-Gas Superior SW66-GIDG_A014 | Service & Calibration Check Task Butterfly / Governor / Ramp Control I/P Transducer | 1 | Y | 01 | 00 |  |  | 1010-295-TIN-0003.pdf
Gidgealpa Gas Satellite - Compression - Compressor Package 3 | GIDG COMP 1010-KX-003 | 1010-KX-003 | Compressor Package IE-Gas Superior SW66-GIDG_A05 | Inspection & Function Check Task Compressor / Engine Lube Oil Level Switch (Controller) | 1 | Y | 01 | 00 |  |  | 1010-295-TIN-0003.pdf
Gidgealpa Gas Satellite - Compression - Compressor Package 3 | GIDG COMP 1010-KX-003 | 1010-KX-003 | Compressor Package IE-Gas Superior SW66-GIDG_A015 | Inspection & Function Check Task Start Valve / Run Fuel Valve Control Air Supply Isolation Solenoid | 1 | Y | 01 | 00 |  |  | 1010-295-TIN-0003.pdf
Gidgealpa Gas Satellite - Compression - Compressor Package 3 | GIDG COMP 1010-KX-003 | 1010-KX-003 | Compressor Package IE-Gas Superior SW66-GIDG_A07 | Inspection & Calibration Check Task Compressor Suction / Interstage /Discharge Scrubber Level Transmitters | 1 | Y | 01 | 00 |  |  | 1010-295-TIN-0003.pdf
Gidgealpa Gas Satellite - Compression - Compressor Package 3 | GIDG COMP 1010-KX-003 | 1010-KX-003 | Compressor Package IE-Gas Superior SW66-GIDG_A013 | Inspection & Calibration Check Suction / Interstage / Discharge Scrubber Pressure Transmitters (AL / SD) | 1 | Y | 01 | 00 |  |  | 1010-295-TIN-0003.pdf
Gidgealpa Gas Satellite - Compression - Compressor Package 3 | GIDG COMP 1010-KX-003 | 1010-KX-003 | Compressor Package IE-Gas Superior SW66-GIDG_A020 | Service & Calibration Task Starter Gas Shuttle Valve | 1 | Y | 01 | 00 |  |  | 1010-295-TIN-0003.pdf
Gidgealpa Gas Satellite - Compression - Compressor Package 3 | GIDG COMP 1010-KX-003 | 1010-KX-003 | Compressor Package IE-Gas Superior SW66-GIDG_A017 | Service & Calibration Task Compressor Recycle Valve I/P Transducer | 1 | Y | 01 | 00 |  |  | 1010-295-TIN-0003.pdf
Gidgealpa Gas Satellite - Compression - Compressor Package 3 | GIDG COMP 1010-KX-003 | 1010-KX-003 | Compressor Package IE-Gas Superior SW66-GIDG_A012 | Inspection & Calibration Check Suction / Interstage / Discharge Scrubber Pressure Transmitters (to PIC) | 1 | Y | 01 | 00 |  |  | 1010-295-TIN-0003.pdf
Gidgealpa Gas Satellite - Compression - Compressor Package 3 | GIDG COMP 1010-KX-003 | 1010-KX-003 | Compressor Package IE-Gas Superior SW66-GIDG_A09 | Service & Calibration Task Compressor Lubricator Flow Switch Low Low | 1 | Y | 01 | 00 |  |  | 1010-295-TIN-0003.pdf
Gidgealpa Gas Satellite - Compression - Compressor Package 3 | GIDG COMP 1010-KX-003 | 1010-KX-003 | Compressor Package IE-Gas Superior SW66-GIDG_A04 | Service & Calibration Task Engine / Compressor Oil Filter Differential Pressure Switch | 1 | Y | 01 | 00 |  |  | 1010-295-TIN-0003.pdf
Gidgealpa Gas Satellite - Compression - Compressor Package 3 | GIDG COMP 1010-KX-003 | 1010-KX-003 | Compressor Package IE-Gas Superior SW66-GIDG_A019 | Service & Calibration Check Task Butterfly / Ramp Pneumatic Booster Relay (3:1) | 1 | Y | 01 | 00 |  |  | 1010-295-TIN-0003.pdf
Gidgealpa Gas Satellite - Compression - Compressor Package 3 | GIDG COMP 1010-KX-003 | 1010-KX-003 | Compressor Package IE-Gas Superior SW66-GIDG_A011 | Inspection & Calibration Check Compressor Inlet / Fuel Gas / Engine Manifold Pressure Transmitters | 1 | Y | 01 | 00 |  |  | 1010-295-TIN-0003.pdf
Gidgealpa Gas Satellite - Compression - Compressor Package 3 | GIDG COMP 1010-KX-003 | 1010-KX-003 | Compressor Package IE-Gas Superior SW66-GIDG_A021 | Inspection & Function Check Package Engine Overspeed Shutdown | 1 | Y | 01 | 00 |  |  | 1010-295-TIN-0003.pdf
Gidgealpa Gas Satellite - Compression - Compressor Package 3 | GIDG COMP 1010-KX-003 | 1010-KX-003 | Compressor Package IE-Gas Superior SW66-GIDG_A011 | Inspection & Calibration Check Compressor Inlet / Fuel Gas / Engine Manifold Pressure Transmitters | 1 | Y | 01 | 00 |  |  | 1010-295-TIN-0003.pdf
Gidgealpa Gas Satellite - Compression - Compressor Package 3 | GIDG COMP 1010-KX-003 | 1010-KX-003 | Compressor Package IE-Gas Superior SW66-GIDG_A03 | Service & Calibration Task Engine / Compressor Lube Oil Pressure Switch | 1 | Y | 01 | 00 |  |  | 1010-295-TIN-0003.pdf
Gidgealpa Gas Satellite - Compression - Compressor Package 3 | GIDG COMP 1010-KX-003 | 1010-KX-003 | Compressor Package IE-Gas Superior SW66-GIDG_A05 | Inspection & Function Check Task Compressor / Engine Lube Oil Level Switch (Controller) | 1 | Y | 01 | 00 |  |  | 1010-295-TIN-0003.pdf
Gidgealpa Gas Satellite - Compression - Compressor Package 3 | GIDG COMP 1010-KX-003 | 1010-KX-003 | Compressor Package IE-Gas Superior SW66-GIDG_A06 | Inspection & Function Check Task Engine Surge Tank Level Switch Low Low | 1 | Y | 01 | 00 |  |  | 1010-295-TIN-0003.pdf
Gidgealpa Gas Satellite - Compression - Compressor Package 3 | GIDG COMP 1010-KX-003 | 1010-KX-003 | Compressor Package IE-Gas Superior SW66-GIDG_A01 | Inspection & Calibration Check Engine Temperature RTDs (Lube Oil, Turbo & Jacket Water) | 1 | Y | 01 | 00 |  |  | 1010-295-TIN-0003.pdf
Gidgealpa Gas Satellite - Compression - Compressor Package 3 | GIDG COMP 1010-KX-003 | 1010-KX-003 | Compressor Package IE-Gas Superior SW66-GIDG_A016 | Inspection & Calibration Check Task Compressor / Engine Package Vibration Switches | 1 | Y | 01 | 00 |  |  | 1010-295-TIN-0003.pdf
Gidgealpa Gas Satellite - Compression - Compressor Package 3 | GIDG COMP 1010-KX-003 | 1010-KX-003 | Compressor Package IE-Gas Superior SW66-GIDG_A04 | Service & Calibration Task Engine / Compressor Oil Filter Differential Pressure Switch | 1 | Y | 01 | 00 |  |  | 1010-295-TIN-0003.pdf
Gidgealpa Gas Satellite - Compression - Compressor Package 3 | GIDG COMP 1010-KX-003 | 1010-KX-003 | Compressor Package IE-Gas Superior SW66-GIDG_A08 | Inspection & Function Check Task Compressor / Engine Cooling Water Flow Switches | 1 | Y | 01 | 00 |  |  | 1010-295-TIN-0003.pdf
Gidgealpa Gas Satellite - Compression - Compressor Package 3 | GIDG COMP 1010-K-001 | 1010-K-001 | Compressor-Gas Superior SW66-GIDG_A014 | Inspect/Check/Torque Fastener Torque - Frame/Cylinders | 1 | Y | 4 | 00 |  |  | 0001-296-TIN-0068.pdf
Gidgealpa Gas Satellite - Compression - Compressor Package 3 | GIDG COMP 1010-K-001 | 1010-K-001 | Compressor-Gas Superior SW66-GIDG_A031 | Replace Piston Rings / Rider Wearbands | 3 | Y | 4 | 00 |  |  | 0001-296-TIN-0068.pdf
Gidgealpa Gas Satellite - Compression - Compressor Package 3 | GIDG COMP 1010-K-001 | 1010-K-001 | Compressor-Gas Superior SW66-GIDG_A030 | Inspect/Record Cylinder Bore/Liner | 3 | Y | 4 | 00 |  |  | 0001-296-TIN-0068.pdf
Gidgealpa Gas Satellite - Compression - Compressor Package 3 | GIDG COMP 1010-K-001 | 1010-K-001 | Compressor-Gas Superior SW66-GIDG_A017 | Lubricate VVCP Threads | 1 | Y | 4 | 00 |  |  | 0001-296-TIN-0068.pdf
Gidgealpa Gas Satellite - Compression - Compressor Package 3 | GIDG COMP 1010-K-001 | 1010-K-001 | Compressor-Gas Superior SW66-GIDG_A035 | Strip/Inspect/Repair VVCP | 12 | Y | 4 | 00 |  |  | 0001-296-TIN-0068.pdf
Gidgealpa Gas Satellite - Compression - Compressor Package 3 | GIDG COMP 1010-K-001 | 1010-K-001 | Compressor-Gas Superior SW66-GIDG_A041 | Inspect/Replace Cylinder Liner | 12 | Y | 4 | 00 |  |  | 0001-296-TIN-0068.pdf
Gidgealpa Gas Satellite - Compression - Compressor Package 3 | GIDG COMP 1010-K-001 | 1010-K-001 | Compressor-Gas Superior SW66-GIDG_A07 | Replace Supply filter to cylinder oil header tank | 6 | M | 4 | 00 |  |  | 0001-296-TIN-0068.pdf
Gidgealpa Gas Satellite - Compression - Compressor Package 3 | GIDG COMP 1010-K-001 | 1010-K-001 | Compressor-Gas Superior SW66-GIDG_A029 | Inspect/Replace on condition Piston Rods | 3 | Y | 4 | 00 |  |  | 0001-296-TIN-0068.pdf
Gidgealpa Gas Satellite - Compression - Compressor Package 3 | GIDG COMP 1010-K-001 | 1010-K-001 | Compressor-Gas Superior SW66-GIDG_A013 | Check/Record Piston Rod Runout | 1 | Y | 4 | 00 |  |  | 0001-296-TIN-0068.pdf
Gidgealpa Gas Satellite - Compression - Compressor Package 3 | GIDG COMP 1010-K-001 | 1010-K-001 | Compressor-Gas Superior SW66-GIDG_A032 | Replace Oil Wiper - Piston Rods | 3 | Y | 4 | 00 |  |  | 0001-296-TIN-0068.pdf
Gidgealpa Gas Satellite - Compression - Compressor Package 3 | GIDG COMP 1010-K-001 | 1010-K-001 | Compressor-Gas Superior SW66-GIDG_A042 | Inspect Process gas inlet screen (cone strainers) if fitted on each stage | 12 | Y | 4 | 00 |  |  | 0001-296-TIN-0068.pdf
Gidgealpa Gas Satellite - Compression - Compressor Package 3 | GIDG COMP 1010-K-001 | 1010-K-001 | Compressor-Gas Superior SW66-GIDG_A010 | Inspect/Fix Package fusible loop tubing (rubs, free spans, vibration) | 1 | Y | 4 | 00 |  |  | 0001-296-TIN-0068.pdf
Gidgealpa Gas Satellite - Compression - Compressor Package 3 | GIDG COMP 1010-K-001 | 1010-K-001 | Compressor-Gas Superior SW66-GIDG_A045 | Measure/Record Compressor Balance | 12 | Y | 4 | 00 |  |  | 0001-296-TIN-0068.pdf
Gidgealpa Gas Satellite - Compression - Compressor Package 3 | GIDG COMP 1010-K-001 | 1010-K-001 | Compressor-Gas Superior SW66-GIDG_A022 | Check Looseness/Pitch After/Aux Cooler fan blades and hubs | 1 | Y | 4 | 00 |  |  | 0001-296-TIN-0068.pdf
Gidgealpa Gas Satellite - Compression - Compressor Package 3 | GIDG COMP 1010-K-001 | 1010-K-001 | Compressor-Gas Superior SW66-GIDG_A046 | Overhaul Crankcase Over-pressure Relief Valves | 12 | Y | 4 | 00 |  |  | 0001-296-TIN-0068.pdf
Gidgealpa Gas Satellite - Compression - Compressor Package 3 | GIDG COMP 1010-K-001 | 1010-K-001 | Compressor-Gas Superior SW66-GIDG_A024 | Inspect/Check/Adjust Coupling/Alignment | 3 | Y | 4 | 00 |  |  | 0001-296-TIN-0068.pdf
Gidgealpa Gas Satellite - Compression - Compressor Package 3 | GIDG COMP 1010-K-001 | 1010-K-001 | Compressor-Gas Superior SW66-GIDG_A08 | Inspect Walk-around Inspection (Fluid/gas leaks, unusual noise, excessive vibration and loose or missing fasteners) | 6 | M | 4 | 00 |  |  | 0001-296-TIN-0068.pdf
Gidgealpa Gas Satellite - Compression - Compressor Package 3 | GIDG COMP 1010-K-001 | 1010-K-001 | Compressor-Gas Superior SW66-GIDG_A027 | Replace Divider Blocks | 3 | Y | 4 | 00 |  |  | 0001-296-TIN-0068.pdf
Gidgealpa Gas Satellite - Compression - Compressor Package 3 | GIDG COMP 1010-K-001 | 1010-K-001 | Compressor-Gas Superior SW66-GIDG_A03 | Inspect/Clean Lubricator Box Sintered Element | 6 | M | 4 | 00 |  |  | 0001-296-TIN-0068.pdf
Gidgealpa Gas Satellite - Compression - Compressor Package 3 | GIDG COMP 1010-K-001 | 1010-K-001 | Compressor-Gas Superior SW66-GIDG_A019 | Inspect Lubricator Cams/Followers/Gears/Drive Coupling | 1 | Y | 4 | 00 |  |  | 0001-296-TIN-0068.pdf
Gidgealpa Gas Satellite - Compression - Compressor Package 3 | GIDG COMP 1010-K-001 | 1010-K-001 | Compressor-Gas Superior SW66-GIDG_A026 | Replace Lubricator Pump Elements | 3 | Y | 4 | 00 |  |  | 0001-296-TIN-0068.pdf
Gidgealpa Gas Satellite - Compression - Compressor Package 3 | GIDG COMP 1010-K-001 | 1010-K-001 | Compressor-Gas Superior SW66-GIDG_A021 | Check Force Lubrication Circuit flow to each point. Hand pump. | 1 | Y | 4 | 00 |  |  | 0001-296-TIN-0068.pdf
Gidgealpa Gas Satellite - Compression - Compressor Package 3 | GIDG COMP 1010-K-001 | 1010-K-001 | Compressor-Gas Superior SW66-GIDG_A033 | Replace Force Lubrication Circuit Check Valves / NRV's | 3 | Y | 4 | 00 |  |  | 0001-296-TIN-0068.pdf
Gidgealpa Gas Satellite - Compression - Compressor Package 3 | GIDG COMP 1010-K-001 | 1010-K-001 | Compressor-Gas Superior SW66-GIDG_A04 | Replace Lube Oil Filter and Housing Gasket | 6 | M | 4 | 00 |  |  | 0001-296-TIN-0068.pdf
Gidgealpa Gas Satellite - Compression - Compressor Package 3 | GIDG COMP 1010-K-001 | 1010-K-001 | Compressor-Gas Superior SW66-GIDG_A040 | Replace Lubricator Box | 12 | Y | 4 | 00 |  |  | 0001-296-TIN-0068.pdf
Gidgealpa Gas Satellite - Compression - Compressor Package 3 | GIDG COMP 1010-K-001 | 1010-K-001 | Compressor-Gas Superior SW66-GIDG_A02 | Flush/Clean/Replace Lubricator Box Housing Oil | 6 | M | 4 | 00 |  |  | 0001-296-TIN-0068.pdf
Gidgealpa Gas Satellite - Compression - Compressor Package 3 | GIDG COMP 1010-K-001 | 1010-K-001 | Compressor-Gas Superior SW66-GIDG_A09 | Clean when oil replaced Compressor Frame Lubrication Circuit Y-Strainer | 1 | Y | 4 | 00 |  |  | 0001-296-TIN-0068.pdf
Gidgealpa Gas Satellite - Compression - Compressor Package 3 | GIDG COMP 1010-K-001 | 1010-K-001 | Compressor-Gas Superior SW66-GIDG_A038 | Inspect/Replace Oil Strainer | 12 | Y | 4 | 00 |  |  | 0001-296-TIN-0068.pdf
Gidgealpa Gas Satellite - Compression - Compressor Package 3 | GIDG COMP 1010-K-001 | 1010-K-001 | Compressor-Gas Superior SW66-GIDG_A06 | Replace Supply filter to frame oil header tank | 6 | M | 4 | 00 |  |  | 0001-296-TIN-0068.pdf
Gidgealpa Gas Satellite - Compression - Compressor Package 3 | GIDG COMP 1010-K-001 | 1010-K-001 | Compressor-Gas Superior SW66-GIDG_A011 | Clean/Replace Frame Breather Element | 1 | Y | 4 | 00 |  |  | 0001-296-TIN-0068.pdf
Gidgealpa Gas Satellite - Compression - Compressor Package 3 | GIDG COMP 1010-K-001 | 1010-K-001 | Compressor-Gas Superior SW66-GIDG_A05 | Check/Adjust Oil Leveller | 6 | M | 4 | 00 |  |  | 0001-296-TIN-0068.pdf
Gidgealpa Gas Satellite - Compression - Compressor Package 3 | GIDG COMP 1010-K-001 | 1010-K-001 | Compressor-Gas Superior SW66-GIDG_A015 | Replace Compressor Valves - Gaskets/Seals | 1 | Y | 4 | 00 |  |  | 0001-296-TIN-0068.pdf
Gidgealpa Gas Satellite - Compression - Compressor Package 3 | GIDG COMP 1010-K-001 | 1010-K-001 | Compressor-Gas Superior SW66-GIDG_A016 | Inspect/Clean Valve Pockets and Cylinder Gas Passages | 1 | Y | 4 | 00 |  |  | 0001-296-TIN-0068.pdf
Gidgealpa Gas Satellite - Compression - Compressor Package 3 | GIDG COMP 1010-K-001 | 1010-K-001 | Compressor-Gas Superior SW66-GIDG_A018 | Inspect/Clean Packing Vents/Drains | 1 | Y | 4 | 00 |  |  | 0001-296-TIN-0068.pdf
Gidgealpa Gas Satellite - Compression - Compressor Package 3 | GIDG COMP 1010-K-001 | 1010-K-001 | Compressor-Gas Superior SW66-GIDG_A028 | Replace Packing Assemblies | 3 | Y | 4 | 00 |  |  | 0001-296-TIN-0068.pdf
Gidgealpa Gas Satellite - Compression - Compressor Package 3 | GIDG COMP 1010-K-001 | 1010-K-001 | Compressor-Gas Superior SW66-GIDG_A043 | Replace Drive Chain/s | 12 | Y | 4 | 00 |  |  | 0001-296-TIN-0068.pdf
Gidgealpa Gas Satellite - Compression - Compressor Package 3 | GIDG COMP 1010-K-001 | 1010-K-001 | Compressor-Gas Superior SW66-GIDG_A020 | Inspect/Check/Adjust Drive Chain/s | 1 | Y | 4 | 00 |  |  | 0001-296-TIN-0068.pdf
Gidgealpa Gas Satellite - Compression - Compressor Package 3 | GIDG COMP 1010-K-001 | 1010-K-001 | Compressor-Gas Superior SW66-GIDG_A034 | Inspect/Replace Auxiliary Drive Chain Sprockets | 3 | Y | 4 | 00 |  |  | 0001-296-TIN-0068.pdf
Gidgealpa Gas Satellite - Compression - Compressor Package 3 | GIDG COMP 1010-K-001 | 1010-K-001 | Compressor-Gas Superior SW66-GIDG_A039 | Inspect/Replace Piston | 12 | Y | 4 | 00 |  |  | 0001-296-TIN-0068.pdf
Gidgealpa Gas Satellite - Compression - Compressor Package 3 | GIDG COMP 1010-K-001 | 1010-K-001 | Compressor-Gas Superior SW66-GIDG_A025 | Inspect Piston and Piston Ring Grooves | 3 | Y | 4 | 00 |  |  | 0001-296-TIN-0068.pdf
Gidgealpa Gas Satellite - Compression - Compressor Package 3 | GIDG COMP 1010-K-001 | 1010-K-001 | Compressor-Gas Superior SW66-GIDG_A044 | Inspect/Clean/Replace Crossheads, Pins, Crosshead Bushings and Nuts | 12 | Y | 4 | 00 |  |  | 0001-296-TIN-0068.pdf
Gidgealpa Gas Satellite - Compression - Compressor Package 3 | GIDG COMP 1010-K-001 | 1010-K-001 | Compressor-Gas Superior SW66-GIDG_A012 | Check/Record Crosshead to Guide Clearance | 1 | Y | 4 | 00 |  |  | 0001-296-TIN-0068.pdf
Gidgealpa Gas Satellite - Compression - Compressor Package 3 | GIDG COMP 1010-K-001 | 1010-K-001 | Compressor-Gas Superior SW66-GIDG_A01 | Check condition/Replace Compressor Frame Oil | 6 | M | 4 | 00 |  |  | 0001-296-TIN-0068.pdf
Gidgealpa Gas Satellite - Compression - Compressor Package 3 | GIDG COMP 1010-K-001 | 1010-K-001 | Compressor-Gas Superior SW66-GIDG_A036 | Inspect/Replace Main Bearings and Thrust Bearings | 12 | Y | 4 | 00 |  |  | 0001-296-TIN-0068.pdf
Gidgealpa Gas Satellite - Compression - Compressor Package 3 | GIDG COMP 1010-K-001 | 1010-K-001 | Compressor-Gas Superior SW66-GIDG_A023 | Replace Compressor Frame Oil | 3 | Y | 4 | 00 |  |  | 0001-296-TIN-0068.pdf
Gidgealpa Gas Satellite - Compression - Compressor Package 3 | GIDG COMP 1010-K-001 | 1010-K-001 | Compressor-Gas Superior SW66-GIDG_A037 | Inspect/Replace Connecting Rod Bearings/Bushings | 12 | Y | 4 | 00 |  |  | 0001-296-TIN-0068.pdf
Gidgealpa Gas Satellite - Compression - Compressor Package 3 | GIDG COMP 1010-E-003 | 1010-E-003 | Cooler-Compressor-GIDG_A011 | Remove the drain plug and using a metal rod | 1 | Y | 01 | 00 |  |  | 2251905.docx
Gidgealpa Gas Satellite - Compression - Compressor Package 3 | GIDG COMP 1010-E-003 | 1010-E-003 | Cooler-Compressor-GIDG_A07 | Install belt guards after belt inspection | 1 | Y | 4 | 00 |  |  | 2223330.docx
Gidgealpa Gas Satellite - Compression - Compressor Package 3 | GIDG COMP 1010-E-003 | 1010-E-003 | Cooler-Compressor-GIDG_A08 | Re-grease fan mast bearings if grease nipple fitted | 1 | Y | 4 | 00 |  |  | 2223330.docx
Gidgealpa Gas Satellite - Compression - Compressor Package 3 | GIDG COMP 1010-E-003 | 1010-E-003 | Cooler-Compressor-GIDG_A015 | Inspect purged grease for evidence of metal particles or contamination | 1 | Y | 01 | 00 |  |  | 2251905.docx
Gidgealpa Gas Satellite - Compression - Compressor Package 3 | GIDG COMP 1010-E-003 | 1010-E-003 | Cooler-Compressor-GIDG_A02 | Remove belt guard to access belts | 1 | Y | 4 | 00 |  |  | 2223330.docx
Gidgealpa Gas Satellite - Compression - Compressor Package 3 | GIDG COMP 1010-E-003 | 1010-E-003 | Cooler-Compressor-GIDG_A016 | Replace the drain plug | 1 | Y | 01 | 00 |  |  | 2251905.docx
Gidgealpa Gas Satellite - Compression - Compressor Package 3 | GIDG COMP 1010-E-003 | 1010-E-003 | Cooler-Compressor-GIDG_A09 | Check for leaking grease lines and repair if required | 1 | Y | 4 | 00 |  |  | 2223330.docx
Gidgealpa Gas Satellite - Compression - Compressor Package 3 | GIDG COMP 1010-E-003 | 1010-E-003 | Cooler-Compressor-GIDG_A010 | Clear the drain plug, grease nipple and grease gun nozzle to prevent introducing contaminants or abrasives into the bearing | 1 | Y | 01 | 00 |  |  | 2251905.docx
Gidgealpa Gas Satellite - Compression - Compressor Package 3 | GIDG COMP 1010-E-003 | 1010-E-003 | Cooler-Compressor-GIDG_A06 | Check and adjust the belt tension as required. | 1 | Y | 4 | 00 |  |  | 2223330.docx
Gidgealpa Gas Satellite - Compression - Compressor Package 3 | GIDG COMP 1010-E-003 | 1010-E-003 | Cooler-Compressor-GIDG_A04 | Replace belt if tooth thickness is less than 75% of new or is worn by required | 1 | Y | 4 | 00 |  |  | 2223330.docx
Gidgealpa Gas Satellite - Compression - Compressor Package 3 | GIDG COMP 1010-E-003 | 1010-E-003 | Cooler-Compressor-GIDG_A013 | Re-grease motor bearings | 1 | Y | 01 | 00 |  |  | 2251905.docx
Gidgealpa Gas Satellite - Compression - Compressor Package 3 | GIDG COMP 1010-E-003 | 1010-E-003 | Cooler-Compressor-GIDG_A03 | Inspect belt for cracks, fraying and missing teeth | 1 | Y | 4 | 00 |  |  | 2223330.docx
Gidgealpa Gas Satellite - Compression - Compressor Package 3 | GIDG COMP 1010-E-003 | 1010-E-003 | Cooler-Compressor-GIDG_A05 | Inspect pulleys for excessive wear | 1 | Y | 4 | 00 |  |  | 2223330.docx
Gidgealpa Gas Satellite - Compression - Compressor Package 3 | GIDG COMP 1010-E-003 | 1010-E-003 | Cooler-Compressor-GIDG_A012 | Clean old grease from the drain opening | 1 | Y | 01 | 00 |  |  | 2251905.docx
Gidgealpa Gas Satellite - Compression - Compressor Package 3 | GIDG COMP 1010-E-003 | 1010-E-003 | Cooler-Compressor-GIDG_A014 | Clean the grease outlet of purged | 1 | Y | 01 | 00 |  |  | 2251905.docx
Gidgealpa Gas Satellite - Compression - Compressor Package 3 | GIDG COMP 1010-E-003 | 1010-E-003 | Cooler-Compressor-GIDG_A01 | Erect mobile scaffold to access belt drive | 1 | Y | 4 | 00 |  |  | 2223330.docx
Gidgealpa Gas Satellite - Compression - Compressor Package 3 | GIDG COMP 1010-E-003 | 1010-E-003 | Cooler-Compressor-GIDG_A017 | Function test and calibrate vibration switch | 1 | Y | 01 | 00 |  |  | 2251905.docx
Gidgealpa Gas Satellite - Compression - Compressor Package 3 | GIDG COMP 1010-E-003 | 1010-E-003 | Cooler-Compressor-GIDG_A018 | Check vibration switch mounting bolt for tightness | 1 | Y | 01 | 00 |  |  | 2251905.docx
Gidgealpa Gas Satellite - Compression - Compressor Package 3 | GIDG COMP 1010-E-003 | 1010-E-003 | Cooler-Compressor-GIDG_A021 | Manually trip switch and confirm alarm functions correctly | 1 | Y | 01 | 00 |  |  | 2251905.docx
Gidgealpa Gas Satellite - Compression - Compressor Package 3 | GIDG COMP 1010-E-003 | 1010-E-003 | Cooler-Compressor-GIDG_A019 | Inspect cabling and glanding for wear or deterioration of cable | 1 | Y | 01 | 00 |  |  | 2251905.docx
Gidgealpa Gas Satellite - Compression - Compressor Package 3 | GIDG COMP 1010-E-003 | 1010-E-003 | Cooler-Compressor-GIDG_A020 | Inspect internals of vibration switch for component security | 1 | Y | 01 | 00 |  |  | 2251905.docx
Gidgealpa Gas Satellite - Compression - Compressor Package 3 | GIDG COMP 1010-E-002 | 1010-E-002 | Cooler-Compressor-GIDG_A018 | Check vibration switch mounting bolt for tightness | 1 | Y | 01 | 00 |  |  | 2251905.docx
Gidgealpa Gas Satellite - Compression - Compressor Package 3 | GIDG COMP 1010-E-002 | 1010-E-002 | Cooler-Compressor-GIDG_A017 | Function test and calibrate vibration switch | 1 | Y | 01 | 00 |  |  | 2251905.docx
Gidgealpa Gas Satellite - Compression - Compressor Package 3 | GIDG COMP 1010-E-002 | 1010-E-002 | Cooler-Compressor-GIDG_A020 | Inspect internals of vibration switch for component security | 1 | Y | 01 | 00 |  |  | 2251905.docx
Gidgealpa Gas Satellite - Compression - Compressor Package 3 | GIDG COMP 1010-E-002 | 1010-E-002 | Cooler-Compressor-GIDG_A019 | Inspect cabling and glanding for wear or deterioration of cable | 1 | Y | 01 | 00 |  |  | 2251905.docx
Gidgealpa Gas Satellite - Compression - Compressor Package 3 | GIDG COMP 1010-E-002 | 1010-E-002 | Cooler-Compressor-GIDG_A021 | Manually trip switch and confirm alarm functions correctly | 1 | Y | 01 | 00 |  |  | 2251905.docx
Gidgealpa Gas Satellite - Compression - Compressor Package 3 | GIDG COMP 1010-E-002 | 1010-E-002 | Cooler-Compressor-GIDG_A014 | Clean the grease outlet of purged | 1 | Y | 01 | 00 |  |  | 2251905.docx
Gidgealpa Gas Satellite - Compression - Compressor Package 3 | GIDG COMP 1010-E-002 | 1010-E-002 | Cooler-Compressor-GIDG_A01 | Erect mobile scaffold to access belt drive | 1 | Y | 4 | 00 |  |  | 2223330.docx
Gidgealpa Gas Satellite - Compression - Compressor Package 3 | GIDG COMP 1010-E-002 | 1010-E-002 | Cooler-Compressor-GIDG_A012 | Clean old grease from the drain opening | 1 | Y | 01 | 00 |  |  | 2251905.docx | 001
Gidgealpa Gas Satellite - Compression - Compressor Package 3 | GIDG COMP 1010-E-002 | 1010-E-002 | Cooler-Compressor-GIDG_A03 | Inspect belt for cracks, fraying and missing teeth | 1 | Y | 4 | 00 |  |  | 2223330.docx
Gidgealpa Gas Satellite - Compression - Compressor Package 3 | GIDG COMP 1010-E-002 | 1010-E-002 | Cooler-Compressor-GIDG_A06 | Check and adjust the belt tension as required. | 1 | Y | 4 | 00 |  |  | 2223330.docx
Gidgealpa Gas Satellite - Compression - Compressor Package 3 | GIDG COMP 1010-E-002 | 1010-E-002 | Cooler-Compressor-GIDG_A013 | Re-grease motor bearings | 1 | Y | 01 | 00 |  |  | 2251905.docx
Gidgealpa Gas Satellite - Compression - Compressor Package 3 | GIDG COMP 1010-E-002 | 1010-E-002 | Cooler-Compressor-GIDG_A07 | Install belt guards after belt inspection | 1 | Y | 4 | 00 |  |  | 2223330.docx
Gidgealpa Gas Satellite - Compression - Compressor Package 3 | GIDG COMP 1010-E-002 | 1010-E-002 | Cooler-Compressor-GIDG_A016 | Replace the drain plug | 1 | Y | 01 | 00 |  |  | 2251905.docx
Gidgealpa Gas Satellite - Compression - Compressor Package 3 | GIDG COMP 1010-E-002 | 1010-E-002 | Cooler-Compressor-GIDG_A09 | Check for leaking grease lines and repair if required | 1 | Y | 4 | 00 |  |  | 2223330.docx
Gidgealpa Gas Satellite - Compression - Compressor Package 3 | GIDG COMP 1010-E-002 | 1010-E-002 | Cooler-Compressor-GIDG_A015 | Inspect purged grease for evidence of metal particles or contamination | 1 | Y | 01 | 00 |  |  | 2251905.docx
Gidgealpa Gas Satellite - Compression - Compressor Package 3 | GIDG COMP 1010-E-002 | 1010-E-002 | Cooler-Compressor-GIDG_A010 | Clear the drain plug, grease nipple and grease gun nozzle to prevent introducing contaminants or abrasives into the bearing | 1 | Y | 01 | 00 |  |  | 2251905.docx
Gidgealpa Gas Satellite - Compression - Compressor Package 3 | GIDG COMP 1010-E-002 | 1010-E-002 | Cooler-Compressor-GIDG_A05 | Inspect pulleys for excessive wear | 1 | Y | 4 | 00 |  |  | 2223330.docx
Gidgealpa Gas Satellite - Compression - Compressor Package 3 | GIDG COMP 1010-E-002 | 1010-E-002 | Cooler-Compressor-GIDG_A011 | Remove the drain plug and using a metal rod | 1 | Y | 01 | 00 |  |  | 2251905.docx
Gidgealpa Gas Satellite - Compression - Compressor Package 3 | GIDG COMP 1010-E-002 | 1010-E-002 | Cooler-Compressor-GIDG_A04 | Replace belt if tooth thickness is less than 75% of new or is worn by required | 1 | Y | 4 | 00 |  |  | 2223330.docx
Gidgealpa Gas Satellite - Compression - Compressor Package 3 | GIDG COMP 1010-E-002 | 1010-E-002 | Cooler-Compressor-GIDG_A08 | Re-grease fan mast bearings if grease nipple fitted | 1 | Y | 4 | 00 |  |  | 2223330.docx
Gidgealpa Gas Satellite - Compression - HP Compressor Package 1 | GIDG COMP 1010-KX-001 | 1010-KX-001 | Satellite-COM-OEC-GIDG_A01 | Check Compressor crank case lube oil level and the header tank level (fill as required) | 2 | D | 44 | 01 | 1010-KX-001 2D-44-01- |  | OEC Tasks List
Gidgealpa Gas Satellite - Compression - HP Compressor Package 1 | GIDG COMP 1010-KX-001 | 1010-KX-001 | Satellite-COM-OEC-GIDG_A06 | Check lube oil filter DP | 2 | D | 44 | 01 | 1010-KX-001 2D-44-01- |  | OEC Tasks List
Gidgealpa Gas Satellite - Compression - HP Compressor Package 1 | GIDG COMP 1010-KX-001 | 1010-KX-001 | Satellite-COM-OEC-GIDG_A05 | Check oil level in lubricator box | 2 | D | 44 | 01 | 1010-KX-001 2D-44-01- |  | OEC Tasks List
Gidgealpa Gas Satellite - Compression - HP Compressor Package 1 | GIDG COMP 1010-KX-001 | 1010-KX-001 | Satellite-COM-OEC-GIDG_A03 | Check Engine crank case lube oil level and the header tank level (fill as required) | 2 | D | 44 | 01 | 1010-KX-001 2D-44-01- |  | OEC Tasks List
Gidgealpa Gas Satellite - Compression - HP Compressor Package 1 | GIDG COMP 1010-KX-001 | 1010-KX-001 | Satellite-COM-OEC-GIDG_A016 | Check for frayed or broken drive belts | 1 | W | 44 | 01 | 1010-KX-001 1W-44-01- |  | OEC Tasks List
Gidgealpa Gas Satellite - Compression - HP Compressor Package 1 | GIDG COMP 1010-KX-001 | 1010-KX-001 | Satellite-COM-OEC-GIDG_A017 | Inspect safety guards for security | 1 | W | 44 | 01 | 1010-KX-001 1W-44-01- |  | OEC Tasks List
Gidgealpa Gas Satellite - Compression - HP Compressor Package 1 | GIDG COMP 1010-KX-001 | 1010-KX-001 | Satellite-COM-OEC-GIDG_A014 | Check cooler for gas and liquid leaks | 1 | W | 44 | 01 | 1010-KX-001 1W-44-01- |  | OEC Tasks List
Gidgealpa Gas Satellite - Compression - HP Compressor Package 1 | GIDG COMP 1010-KX-001 | 1010-KX-001 | Satellite-COM-OEC-GIDG_A02 | Check EJW and AUX header tank and top up as required | 2 | D | 44 | 01 | 1010-KX-001 2D-44-01- |  | OEC Tasks List
Gidgealpa Gas Satellite - Compression - HP Compressor Package 1 | GIDG COMP 1010-KX-001 | 1010-KX-001 | Satellite-COM-OEC-GIDG_A012 | Check lube oil filter DP | 2 | D | 44 | 01 | 1010-KX-001 2D-44-01- |  | OEC Tasks List
Gidgealpa Gas Satellite - Compression - HP Compressor Package 1 | GIDG COMP 1010-KX-001 | 1010-KX-001 | Satellite-COM-OEC-GIDG_A015 | Listen to and observe fan operation checking for belt slippage | 1 | W | 44 | 01 | 1010-KX-001 1W-44-01- |  | OEC Tasks List
Gidgealpa Gas Satellite - Compression - HP Compressor Package 1 | GIDG COMP 1010-KX-001 | 1010-KX-001 | Satellite-COM-OEC-GIDG_A07 | Check oil storage tank and arrange for filling as required | 2 | D | 44 | 01 | 1010-KX-001 2D-44-01- |  | OEC Tasks List
Gidgealpa Gas Satellite - Compression - HP Compressor Package 1 | GIDG COMP 1010-KX-001 | 1010-KX-001 | Satellite-COM-OEC-GIDG_A04 | Blowdown of Bidell level bridles | 2 | D | 44 | 01 | 1010-KX-001 2D-44-01- |  | OEC Tasks List
Gidgealpa Gas Satellite - Compression - Mobile Compressor Package K170 | GIDG COMP K170-CR-0003 | K170-CR-0003 | Crane-Monorail-GIDG_A017 | Inspect the cross travel wheels for wear, lubricate if required | 1 | Y | 21 | 00 |  |  | INSPECT-PM-CR.MO-003628-C-2007.docx
Gidgealpa Gas Satellite - Compression - Mobile Compressor Package K170 | GIDG COMP K170-CR-0002 | K170-CR-0002 | Crane-Jib-GIDG_A06 | Lubricate and re-check the movement | 1 | Y | 21 | 00 |  |  | INSPECT-PM-CR.MO-003628-C-2005.docx
Gidgealpa Gas Satellite - Compression - Mobile Compressor Package K170 | GIDG COMP K170-CR-0002 | K170-CR-0002 | Crane-Jib-GIDG_A011 | Inspect the Jib for bends or twisting due to overload or impact | 1 | Y | 21 | 00 |  |  | INSPECT-PM-CR.MO-003628-C-2005.docx
Gidgealpa Gas Satellite - Compression - Mobile Compressor Package K170 | GIDG COMP K170-CR-0002 | K170-CR-0002 | Crane-Jib-GIDG_A07 | Change out chain block with a replacement that is certified and has a current test tag | 1 | Y | 21 | 00 |  |  | INSPECT-PM-CR.MO-003628-C-2005.docx
Gidgealpa Gas Satellite - Compression - Mobile Compressor Package K170 | GIDG COMP K170-CR-0002 | K170-CR-0002 | Crane-Jib-GIDG_A02 | Ensure Equipment Number is clearly displayed on the Bridge Beam | 1 | Y | 21 | 00 |  |  | INSPECT-PM-CR.MO-003628-C-2005.docx
Gidgealpa Gas Satellite - Compression - Mobile Compressor Package K170 | GIDG COMP K170-CR-0002 | K170-CR-0002 | Crane-Jib-GIDG_A04 | Ensure Direction of travel signage is clearly visible | 1 | Y | 21 | 00 |  |  | INSPECT-PM-CR.MO-003628-C-2005.docx
Gidgealpa Gas Satellite - Compression - Mobile Compressor Package K170 | GIDG COMP K170-CR-0002 | K170-CR-0002 | Crane-Jib-GIDG_A09 | Ensure that any tag details clearly identify the issue | 1 | Y | 21 | 00 |  |  | INSPECT-PM-CR.MO-003628-C-2005.docx
Gidgealpa Gas Satellite - Compression - Mobile Compressor Package K170 | GIDG COMP K170-CR-0002 | K170-CR-0002 | Crane-Jib-GIDG_A01 | Inspect the signage on the crane | 1 | Y | 21 | 00 |  |  | INSPECT-PM-CR.MO-003628-C-2005.docx
Gidgealpa Gas Satellite - Compression - Mobile Compressor Package K170 | GIDG COMP K170-CR-0002 | K170-CR-0002 | Crane-Jib-GIDG_A03 | Ensure Rated Capacity is clearly displayed on the Bridge Beam and Hook | 1 | Y | 21 | 00 |  |  | INSPECT-PM-CR.MO-003628-C-2005.docx
Gidgealpa Gas Satellite - Compression - Mobile Compressor Package K170 | GIDG COMP K170-CR-0002 | K170-CR-0002 | Crane-Jib-GIDG_A013 | Inspect the long travel wheels for wear, lubricate if required | 1 | Y | 21 | 00 |  |  | INSPECT-PM-CR.MO-003628-C-2005.docx
Gidgealpa Gas Satellite - Compression - Mobile Compressor Package K170 | GIDG COMP K170-CR-0002 | K170-CR-0002 | Crane-Jib-GIDG_A05 | Check for free slewing movement through the Jib's full radius | 1 | Y | 21 | 00 |  |  | INSPECT-PM-CR.MO-003628-C-2005.docx
Gidgealpa Gas Satellite - Compression - Mobile Compressor Package K170 | GIDG COMP K170-CR-0002 | K170-CR-0002 | Crane-Jib-GIDG_A010 | Inspect the post for signs of damage from external impact, loss of protective coatings and corrosion | 1 | Y | 21 | 00 |  |  | INSPECT-PM-CR.MO-003628-C-2005.docx
Gidgealpa Gas Satellite - Compression - Mobile Compressor Package K170 | GIDG COMP K170-CR-0002 | K170-CR-0002 | Crane-Jib-GIDG_A08 | Inspect the concrete foundation block for cracks, loose or corroded bolts | 1 | Y | 21 | 00 |  |  | INSPECT-PM-CR.MO-003628-C-2005.docx | 001
Gidgealpa Gas Satellite - Compression - Mobile Compressor Package K170 | GIDG COMP K170-CR-0002 | K170-CR-0002 | Crane-Jib-GIDG_A012 | Inspect jib end stops for distortion, loose or missing bolts or missing buffers | 1 | Y | 21 | 00 |  |  | INSPECT-PM-CR.MO-003628-C-2005.docx
Gidgealpa Gas Satellite - Compression - Mobile Compressor Package K170 | GIDG COMP K170-CR-0001 | K170-CR-0001 | Crane-Jib-GIDG_A07 | Change out chain block with a replacement that is certified and has a current test tag | 1 | Y | 21 | 00 |  |  | INSPECT-PM-CR.MO-003628-C-2005.docx | 001
Gidgealpa Gas Satellite - Compression - Mobile Compressor Package K170 | GIDG COMP K170-CR-0001 | K170-CR-0001 | Crane-Jib-GIDG_A02 | Ensure Equipment Number is clearly displayed on the Bridge Beam | 1 | Y | 21 | 00 |  |  | INSPECT-PM-CR.MO-003628-C-2005.docx
Gidgealpa Gas Satellite - Compression - Mobile Compressor Package K170 | GIDG COMP K170-CR-0001 | K170-CR-0001 | Crane-Jib-GIDG_A04 | Ensure Direction of travel signage is clearly visible | 1 | Y | 21 | 00 |  |  | INSPECT-PM-CR.MO-003628-C-2005.docx
Gidgealpa Gas Satellite - Compression - Mobile Compressor Package K170 | GIDG COMP K170-CR-0001 | K170-CR-0001 | Crane-Jib-GIDG_A09 | Ensure that any tag details clearly identify the issue | 1 | Y | 21 | 00 |  |  | INSPECT-PM-CR.MO-003628-C-2005.docx
Gidgealpa Gas Satellite - Compression - Mobile Compressor Package K170 | GIDG COMP K170-CR-0001 | K170-CR-0001 | Crane-Jib-GIDG_A01 | Inspect the signage on the crane | 1 | Y | 21 | 00 |  |  | INSPECT-PM-CR.MO-003628-C-2005.docx
Gidgealpa Gas Satellite - Compression - Mobile Compressor Package K170 | GIDG COMP K170-CR-0001 | K170-CR-0001 | Crane-Jib-GIDG_A03 | Ensure Rated Capacity is clearly displayed on the Bridge Beam and Hook | 1 | Y | 21 | 00 |  |  | INSPECT-PM-CR.MO-003628-C-2005.docx | 001
Gidgealpa Gas Satellite - Compression - Mobile Compressor Package K170 | GIDG COMP K170-CR-0001 | K170-CR-0001 | Crane-Jib-GIDG_A011 | Inspect the Jib for bends or twisting due to overload or impact | 1 | Y | 21 | 00 |  |  | INSPECT-PM-CR.MO-003628-C-2005.docx
Gidgealpa Gas Satellite - Compression - Mobile Compressor Package K170 | GIDG COMP K170-CR-0001 | K170-CR-0001 | Crane-Jib-GIDG_A05 | Check for free slewing movement through the Jib's full radius | 1 | Y | 21 | 00 |  |  | INSPECT-PM-CR.MO-003628-C-2005.docx
Gidgealpa Gas Satellite - Compression - Mobile Compressor Package K170 | GIDG COMP K170-CR-0001 | K170-CR-0001 | Crane-Jib-GIDG_A06 | Lubricate and re-check the movement | 1 | Y | 21 | 00 |  |  | INSPECT-PM-CR.MO-003628-C-2005.docx
Gidgealpa Gas Satellite - Compression - Mobile Compressor Package K170 | GIDG COMP K170-CR-0001 | K170-CR-0001 | Crane-Jib-GIDG_A013 | Inspect the long travel wheels for wear, lubricate if required | 1 | Y | 21 | 00 |  |  | INSPECT-PM-CR.MO-003628-C-2005.docx
Gidgealpa Gas Satellite - Compression - Mobile Compressor Package K170 | GIDG COMP K170-CR-0001 | K170-CR-0001 | Crane-Jib-GIDG_A010 | Inspect the post for signs of damage from external impact, loss of protective coatings and corrosion | 1 | Y | 21 | 00 |  |  | INSPECT-PM-CR.MO-003628-C-2005.docx
Gidgealpa Gas Satellite - Compression - Mobile Compressor Package K170 | GIDG COMP K170-CR-0001 | K170-CR-0001 | Crane-Jib-GIDG_A08 | Inspect the concrete foundation block for cracks, loose or corroded bolts | 1 | Y | 21 | 00 |  |  | INSPECT-PM-CR.MO-003628-C-2005.docx
Gidgealpa Gas Satellite - Compression - Mobile Compressor Package K170 | GIDG COMP K170-CR-0001 | K170-CR-0001 | Crane-Jib-GIDG_A012 | Inspect jib end stops for distortion, loose or missing bolts or missing buffers | 1 | Y | 21 | 00 |  |  | INSPECT-PM-CR.MO-003628-C-2005.docx
Gidgealpa Gas Satellite - Compression - Mobile Compressor Package K170 | GIDG COMP K170-CR-0004 | K170-CR-0004 | Crane-Monorail-GIDG_A022 | Inspect end stops for distortion, loose or missing bolts or missing buffers | 1 | Y | 21 | 00 |  |  | INSPECT-PM-CR.MO-003628-C-2007.docx
Gidgealpa Gas Satellite - Compression - Mobile Compressor Package K170 | GIDG COMP K170-CR-0004 | K170-CR-0004 | Crane-Monorail-GIDG_A023 | Repair damaged end stop if possible | 1 | Y | 21 | 00 |  |  | INSPECT-PM-CR.MO-003628-C-2007.docx
Gidgealpa Gas Satellite - Compression - Mobile Compressor Package K170 | GIDG COMP K170-CR-0004 | K170-CR-0004 | Crane-Monorail-GIDG_A020 | Inspect the Bogies and End Carriages for perished or missing buffers and loose bolts | 1 | Y | 21 | 00 |  |  | INSPECT-PM-CR.MO-003628-C-2007.docx
Gidgealpa Gas Satellite - Compression - Mobile Compressor Package K170 | GIDG COMP K170-CR-0004 | K170-CR-0004 | Crane-Monorail-GIDG_A019 | Replace all loose or missing bolts and tighten to the OEM specified torque | 1 | Y | 21 | 00 |  |  | INSPECT-PM-CR.MO-003628-C-2007.docx
Gidgealpa Gas Satellite - Compression - Mobile Compressor Package K170 | GIDG COMP K170-CR-0004 | K170-CR-0004 | Crane-Monorail-GIDG_A014 | Inspect the crab trolley for perished or missing buffers, signs of overload and loose bolts | 1 | Y | 21 | 00 |  |  | INSPECT-PM-CR.MO-003628-C-2007.docx
Gidgealpa Gas Satellite - Compression - Mobile Compressor Package K170 | GIDG COMP K170-CR-0004 | K170-CR-0004 | Crane-Monorail-GIDG_A021 | Inspect the Long Travel Rails and Supports for missing or loose hook bolts or other rail fixings, tighten if possible | 1 | Y | 21 | 00 |  |  | INSPECT-PM-CR.MO-003628-C-2007.docx
Gidgealpa Gas Satellite - Compression - Mobile Compressor Package K170 | GIDG COMP K170-CR-0004 | K170-CR-0004 | Crane-Monorail-GIDG_A02 | Ensure Equipment Number is clearly displayed on the Bridge Beam | 1 | Y | 21 | 00 |  |  | INSPECT-PM-CR.MO-003628-C-2007.docx
Gidgealpa Gas Satellite - Compression - Mobile Compressor Package K170 | GIDG COMP K170-CR-0004 | K170-CR-0004 | Crane-Monorail-GIDG_A01 | Inspect the signage on the crane | 1 | Y | 21 | 00 |  |  | INSPECT-PM-CR.MO-003628-C-2007.docx
Gidgealpa Gas Satellite - Compression - Mobile Compressor Package K170 | GIDG COMP K170-CR-0004 | K170-CR-0004 | Crane-Monorail-GIDG_A03 | Ensure Rated Capacity is clearly displayed on the Bridge Beam and Hook | 1 | Y | 21 | 00 |  |  | INSPECT-PM-CR.MO-003628-C-2007.docx
Gidgealpa Gas Satellite - Compression - Mobile Compressor Package K170 | GIDG COMP K170-CR-0004 | K170-CR-0004 | Crane-Monorail-GIDG_A04 | Operate the long travel chain wheel through the full length of travel to ensure correct operation | 1 | Y | 21 | 00 |  |  | INSPECT-PM-CR.MO-003628-C-2007.docx
Gidgealpa Gas Satellite - Compression - Mobile Compressor Package K170 | GIDG COMP K170-CR-0004 | K170-CR-0004 | Crane-Monorail-GIDG_A015 | Repairs or replacement of bolts and buffers | 1 | Y | 21 | 00 |  |  | INSPECT-PM-CR.MO-003628-C-2007.docx
Gidgealpa Gas Satellite - Compression - Mobile Compressor Package K170 | GIDG COMP K170-CR-0004 | K170-CR-0004 | Crane-Monorail-GIDG_A024 | Inspect the long travel wheels for wear, lubricate if required | 1 | Y | 21 | 00 |  |  | INSPECT-PM-CR.MO-003628-C-2007.docx
Gidgealpa Gas Satellite - Compression - Mobile Compressor Package K170 | GIDG COMP K170-CR-0004 | K170-CR-0004 | Crane-Monorail-GIDG_A016 | Change out chain block with a replacement that is certified and has a current test tag | 1 | Y | 21 | 00 |  |  | INSPECT-PM-CR.MO-003628-C-2007.docx
Gidgealpa Gas Satellite - Compression - Mobile Compressor Package K170 | GIDG COMP K170-CR-0004 | K170-CR-0004 | Crane-Monorail-GIDG_A010 | Remove all foreign material from platforms and walkways | 1 | Y | 21 | 00 |  |  | INSPECT-PM-CR.MO-003628-C-2007.docx
Gidgealpa Gas Satellite - Compression - Mobile Compressor Package K170 | GIDG COMP K170-CR-0004 | K170-CR-0004 | Crane-Monorail-GIDG_A05 | Disassemble and lubricate the long travel drive | 1 | Y | 21 | 00 |  |  | INSPECT-PM-CR.MO-003628-C-2007.docx
Gidgealpa Gas Satellite - Compression - Mobile Compressor Package K170 | GIDG COMP K170-CR-0004 | K170-CR-0004 | Crane-Monorail-GIDG_A011 | Ensure one square metre of clear area is at the foot of all ladders | 1 | Y | 21 | 00 |  |  | INSPECT-PM-CR.MO-003628-C-2007.docx
Gidgealpa Gas Satellite - Compression - Mobile Compressor Package K170 | GIDG COMP K170-CR-0004 | K170-CR-0004 | Crane-Monorail-GIDG_A09 | Ensure the self closing access gates operate correctly | 1 | Y | 21 | 00 |  |  | INSPECT-PM-CR.MO-003628-C-2007.docx
Gidgealpa Gas Satellite - Compression - Mobile Compressor Package K170 | GIDG COMP K170-CR-0004 | K170-CR-0004 | Crane-Monorail-GIDG_A013 | Clean any foreign material build up from running surfaces | 1 | Y | 21 | 00 |  |  | INSPECT-PM-CR.MO-003628-C-2007.docx
Gidgealpa Gas Satellite - Compression - Mobile Compressor Package K170 | GIDG COMP K170-CR-0004 | K170-CR-0004 | Crane-Monorail-GIDG_A012 | Inspect the crane structure and all running surfaces for build up foreign material | 1 | Y | 21 | 00 |  |  | INSPECT-PM-CR.MO-003628-C-2007.docx
Gidgealpa Gas Satellite - Compression - Mobile Compressor Package K170 | GIDG COMP K170-CR-0004 | K170-CR-0004 | Crane-Monorail-GIDG_A07 | Inspect the full length of the hand chain for cracked links or sharp edges or if the chain guide is damaged or missing | 1 | Y | 21 | 00 |  |  | INSPECT-PM-CR.MO-003628-C-2007.docx
Gidgealpa Gas Satellite - Compression - Mobile Compressor Package K170 | GIDG COMP K170-CR-0004 | K170-CR-0004 | Crane-Monorail-GIDG_A017 | Inspect the cross travel wheels for wear, lubricate if required | 1 | Y | 21 | 00 |  |  | INSPECT-PM-CR.MO-003628-C-2007.docx
Gidgealpa Gas Satellite - Compression - Mobile Compressor Package K170 | GIDG COMP K170-CR-0004 | K170-CR-0004 | Crane-Monorail-GIDG_A06 | Re-check the operation | 1 | Y | 21 | 00 |  |  | INSPECT-PM-CR.MO-003628-C-2007.docx
Gidgealpa Gas Satellite - Compression - Mobile Compressor Package K170 | GIDG COMP K170-CR-0004 | K170-CR-0004 | Crane-Monorail-GIDG_A018 | Inspect the bridge beam bolted connections for loose or missing bolts | 1 | Y | 21 | 00 |  |  | INSPECT-PM-CR.MO-003628-C-2007.docx
Gidgealpa Gas Satellite - Compression - Mobile Compressor Package K170 | GIDG COMP K170-CR-0004 | K170-CR-0004 | Crane-Monorail-GIDG_A08 | Inspect the Platforms, Ladders and Walkways for mechanical damage or loose fixings | 1 | Y | 21 | 00 |  |  | INSPECT-PM-CR.MO-003628-C-2007.docx
Gidgealpa Gas Satellite - Compression - Mobile Compressor Package K170 | GIDG COMP K170-CR-0003 | K170-CR-0003 | Crane-Monorail-GIDG_A010 | Remove all foreign material from platforms and walkways | 1 | Y | 21 | 00 |  |  | INSPECT-PM-CR.MO-003628-C-2007.docx | 001
Gidgealpa Gas Satellite - Compression - Mobile Compressor Package K170 | GIDG COMP K170-CR-0003 | K170-CR-0003 | Crane-Monorail-GIDG_A05 | Disassemble and lubricate the long travel drive | 1 | Y | 21 | 00 |  |  | INSPECT-PM-CR.MO-003628-C-2007.docx
Gidgealpa Gas Satellite - Compression - Mobile Compressor Package K170 | GIDG COMP K170-CR-0003 | K170-CR-0003 | Crane-Monorail-GIDG_A016 | Change out chain block with a replacement that is certified and has a current test tag | 1 | Y | 21 | 00 |  |  | INSPECT-PM-CR.MO-003628-C-2007.docx
Gidgealpa Gas Satellite - Compression - Mobile Compressor Package K170 | GIDG COMP K170-CR-0003 | K170-CR-0003 | Crane-Monorail-GIDG_A04 | Operate the long travel chain wheel through the full length of travel to ensure correct operation | 1 | Y | 21 | 00 |  |  | INSPECT-PM-CR.MO-003628-C-2007.docx
Gidgealpa Gas Satellite - Compression - Mobile Compressor Package K170 | GIDG COMP K170-CR-0003 | K170-CR-0003 | Crane-Monorail-GIDG_A015 | Repairs or replacement of bolts and buffers | 1 | Y | 21 | 00 |  |  | INSPECT-PM-CR.MO-003628-C-2007.docx
Gidgealpa Gas Satellite - Compression - Mobile Compressor Package K170 | GIDG COMP K170-CR-0003 | K170-CR-0003 | Crane-Monorail-GIDG_A024 | Inspect the long travel wheels for wear, lubricate if required | 1 | Y | 21 | 00 |  |  | INSPECT-PM-CR.MO-003628-C-2007.docx
Gidgealpa Gas Satellite - Compression - Mobile Compressor Package K170 | GIDG COMP K170-CR-0003 | K170-CR-0003 | Crane-Monorail-GIDG_A019 | Replace all loose or missing bolts and tighten to the OEM specified torque | 1 | Y | 21 | 00 |  |  | INSPECT-PM-CR.MO-003628-C-2007.docx
Gidgealpa Gas Satellite - Compression - Mobile Compressor Package K170 | GIDG COMP K170-CR-0003 | K170-CR-0003 | Crane-Monorail-GIDG_A014 | Inspect the crab trolley for perished or missing buffers, signs of overload and loose bolts | 1 | Y | 21 | 00 |  |  | INSPECT-PM-CR.MO-003628-C-2007.docx
Gidgealpa Gas Satellite - Compression - Mobile Compressor Package K170 | GIDG COMP K170-CR-0003 | K170-CR-0003 | Crane-Monorail-GIDG_A020 | Inspect the Bogies and End Carriages for perished or missing buffers and loose bolts | 1 | Y | 21 | 00 |  |  | INSPECT-PM-CR.MO-003628-C-2007.docx
Gidgealpa Gas Satellite - Compression - Mobile Compressor Package K170 | GIDG COMP K170-CR-0003 | K170-CR-0003 | Crane-Monorail-GIDG_A021 | Inspect the Long Travel Rails and Supports for missing or loose hook bolts or other rail fixings, tighten if possible | 1 | Y | 21 | 00 |  |  | INSPECT-PM-CR.MO-003628-C-2007.docx
Gidgealpa Gas Satellite - Compression - Mobile Compressor Package K170 | GIDG COMP K170-CR-0003 | K170-CR-0003 | Crane-Monorail-GIDG_A023 | Repair damaged end stop if possible | 1 | Y | 21 | 00 |  |  | INSPECT-PM-CR.MO-003628-C-2007.docx
Gidgealpa Gas Satellite - Compression - Mobile Compressor Package K170 | GIDG COMP K170-CR-0003 | K170-CR-0003 | Crane-Monorail-GIDG_A022 | Inspect end stops for distortion, loose or missing bolts or missing buffers | 1 | Y | 21 | 00 |  |  | INSPECT-PM-CR.MO-003628-C-2007.docx
Gidgealpa Gas Satellite - Compression - Mobile Compressor Package K170 | GIDG COMP K170-CR-0003 | K170-CR-0003 | Crane-Monorail-GIDG_A02 | Ensure Equipment Number is clearly displayed on the Bridge Beam | 1 | Y | 21 | 00 |  |  | INSPECT-PM-CR.MO-003628-C-2007.docx
Gidgealpa Gas Satellite - Compression - Mobile Compressor Package K170 | GIDG COMP K170-CR-0003 | K170-CR-0003 | Crane-Monorail-GIDG_A03 | Ensure Rated Capacity is clearly displayed on the Bridge Beam and Hook | 1 | Y | 21 | 00 |  |  | INSPECT-PM-CR.MO-003628-C-2007.docx | 001
Gidgealpa Gas Satellite - Compression - Mobile Compressor Package K170 | GIDG COMP K170-CR-0003 | K170-CR-0003 | Crane-Monorail-GIDG_A01 | Inspect the signage on the crane | 1 | Y | 21 | 00 |  |  | INSPECT-PM-CR.MO-003628-C-2007.docx
Gidgealpa Gas Satellite - Compression - Mobile Compressor Package K170 | GIDG COMP K170-CR-0003 | K170-CR-0003 | Crane-Monorail-GIDG_A018 | Inspect the bridge beam bolted connections for loose or missing bolts | 1 | Y | 21 | 00 |  |  | INSPECT-PM-CR.MO-003628-C-2007.docx
Gidgealpa Gas Satellite - Compression - Mobile Compressor Package K170 | GIDG COMP K170-CR-0003 | K170-CR-0003 | Crane-Monorail-GIDG_A07 | Inspect the full length of the hand chain for cracked links or sharp edges or if the chain guide is damaged or missing | 1 | Y | 21 | 00 |  |  | INSPECT-PM-CR.MO-003628-C-2007.docx
Gidgealpa Gas Satellite - Compression - Mobile Compressor Package K170 | GIDG COMP K170-CR-0003 | K170-CR-0003 | Crane-Monorail-GIDG_A011 | Ensure one square metre of clear area is at the foot of all ladders | 1 | Y | 21 | 00 |  |  | INSPECT-PM-CR.MO-003628-C-2007.docx
Gidgealpa Gas Satellite - Compression - Mobile Compressor Package K170 | GIDG COMP K170-CR-0003 | K170-CR-0003 | Crane-Monorail-GIDG_A012 | Inspect the crane structure and all running surfaces for build up foreign material | 1 | Y | 21 | 00 |  |  | INSPECT-PM-CR.MO-003628-C-2007.docx
Gidgealpa Gas Satellite - Compression - Mobile Compressor Package K170 | GIDG COMP K170-CR-0003 | K170-CR-0003 | Crane-Monorail-GIDG_A08 | Inspect the Platforms, Ladders and Walkways for mechanical damage or loose fixings | 1 | Y | 21 | 00 |  |  | INSPECT-PM-CR.MO-003628-C-2007.docx
Gidgealpa Gas Satellite - Compression - Mobile Compressor Package K170 | GIDG COMP K170-CR-0003 | K170-CR-0003 | Crane-Monorail-GIDG_A013 | Clean any foreign material build up from running surfaces | 1 | Y | 21 | 00 |  |  | INSPECT-PM-CR.MO-003628-C-2007.docx
Gidgealpa Gas Satellite - Compression - Mobile Compressor Package K170 | GIDG COMP K170-CR-0003 | K170-CR-0003 | Crane-Monorail-GIDG_A06 | Re-check the operation | 1 | Y | 21 | 00 |  |  | INSPECT-PM-CR.MO-003628-C-2007.docx
Gidgealpa Gas Satellite - Compression - Mobile Compressor Package K170 | GIDG COMP K170-CR-0003 | K170-CR-0003 | Crane-Monorail-GIDG_A09 | Ensure the self closing access gates operate correctly | 1 | Y | 21 | 00 |  |  | INSPECT-PM-CR.MO-003628-C-2007.docx
Gidgealpa Gas Satellite - Export and Metering - Pig Launcher Gidgealpa to Moomba | GIDG EXP 1010-PG-001 | 1010-PG-001 | Pig Launcher-GIDG_A06 | Valve Leak Rate Monitoring | 12 | M | 07 | 00 |  |  | 2232881.docx
Gidgealpa Gas Satellite - Export and Metering - Pig Launcher Gidgealpa to Moomba | GIDG EXP 1010-PG-001 | 1010-PG-001 | Pig Launcher-GIDG_A010 | Check the condition and serviceability of all drain/vent ports | 12 | M | 07 | 00 |  |  | 2232881.docx
Gidgealpa Gas Satellite - Export and Metering - Pig Launcher Gidgealpa to Moomba | GIDG EXP 1010-PG-001 | 1010-PG-001 | Pig Launcher-GIDG_A04 | Check the condition and serviceability of the Pig Signal(s); verify that all fixings and linkages are secure | 12 | M | 07 | 00 |  |  | 2232881.docx
Gidgealpa Gas Satellite - Export and Metering - Pig Launcher Gidgealpa to Moomba | GIDG EXP 1010-PG-001 | 1010-PG-001 | Pig Launcher-GIDG_A03 | Inspect the condition & serviceability of the barrel pressure gauge(s), check for leaks, physical damage & corrosion | 12 | M | 07 | 00 |  |  | 2232881.docx
Gidgealpa Gas Satellite - Export and Metering - Pig Launcher Gidgealpa to Moomba | GIDG EXP 1010-PG-001 | 1010-PG-001 | Pig Launcher-GIDG_A02 | Function Check Pressure Gauge | 12 | M | 07 | 00 |  |  | 2232881.docx
Gidgealpa Gas Satellite - Export and Metering - Pig Launcher Gidgealpa to Moomba | GIDG EXP 1010-PG-001 | 1010-PG-001 | Pig Launcher-GIDG_A08 | Check the condition and serviceability of the gearbox | 12 | M | 07 | 00 |  |  | 2232881.docx
Gidgealpa Gas Satellite - Export and Metering - Pig Launcher Gidgealpa to Moomba | GIDG EXP 1010-PG-001 | 1010-PG-001 | Pig Launcher-GIDG_A011 | Check Exercise valves that there are no abnormal noises or vibration | 12 | M | 07 | 00 |  |  | 2232881.docx
Gidgealpa Gas Satellite - Export and Metering - Pig Launcher Gidgealpa to Moomba | GIDG EXP 1010-PG-001 | 1010-PG-001 | Pig Launcher-GIDG_A01 | Inspect the condition & serviceability of all piping valves and actuator/gearbox assemblies | 12 | M | 07 | 00 |  |  | 2232881.docx
Gidgealpa Gas Satellite - Export and Metering - Pig Launcher Gidgealpa to Moomba | GIDG EXP 1010-PG-001 | 1010-PG-001 | Pig Launcher-GIDG_A012 | Final check for Valve Leakage | 12 | M | 07 | 00 |  |  | 2232881.docx | 001
Gidgealpa Gas Satellite - Export and Metering - Pig Launcher Gidgealpa to Moomba | GIDG EXP 1010-PG-001 | 1010-PG-001 | Pig Launcher-GIDG_A07 | Grease Valve Stem | 12 | M | 07 | 00 |  |  | 2232881.docx
Gidgealpa Gas Satellite - Export and Metering - Pig Launcher Gidgealpa to Moomba | GIDG EXP 1010-PG-001 | 1010-PG-001 | Pig Launcher-GIDG_A05 | Initial chack for Valve Leakage | 12 | M | 07 | 00 |  |  | 2232881.docx
Gidgealpa Gas Satellite - Export and Metering - Pig Launcher Gidgealpa to Moomba | GIDG EXP 1010-PG-001 | 1010-PG-001 | Pig Launcher-GIDG_A09 | Check the condition and serviceability of the actuator | 12 | M | 07 | 00 |  |  | 2232881.docx
Gidgealpa Gas Satellite - Fuel Gas Supply - Fuel Gas Conditioning Skid | GIDG FUEL 1010-PCV-1211 | 1010-PCV-1211 | Regulator-Gas-GIDG_A011 | Reassemble regulator and pilot | 12 | M | 4 | 00 |  |  | 2232384.docx
Gidgealpa Gas Satellite - Fuel Gas Supply - Fuel Gas Conditioning Skid | GIDG FUEL 1010-PCV-1224 | 1010-PCV-1224 | Regulator-Gas-GIDG_A011 | Reassemble regulator and pilot | 12 | M | 4 | 00 |  |  | 2232384.docx
Gidgealpa Gas Satellite - Fuel Gas Supply - Fuel Gas Conditioning Skid | GIDG FUEL 1010-PCV-1224 | 1010-PCV-1224 | Regulator-Gas-GIDG_A02 | Replace Support pipe | 12 | M | 4 | 00 |  |  | 2232384.docx
Gidgealpa Gas Satellite - Fuel Gas Supply - Fuel Gas Conditioning Skid | GIDG FUEL 1010-PCV-1224 | 1010-PCV-1224 | Regulator-Gas-GIDG_A012 | Ensure that all components are clean and free of contaminants | 12 | M | 4 | 00 |  |  | 2232384.docx
Gidgealpa Gas Satellite - Fuel Gas Supply - Fuel Gas Conditioning Skid | GIDG FUEL 1010-PCV-1224 | 1010-PCV-1224 | Regulator-Gas-GIDG_A07 | Check condition of seals | 12 | M | 4 | 00 |  |  | 2232384.docx
Gidgealpa Gas Satellite - Fuel Gas Supply - Fuel Gas Conditioning Skid | GIDG FUEL 1010-PCV-1224 | 1010-PCV-1224 | Regulator-Gas-GIDG_A03 | Check Gramaphone on Flange faces before installing blank flange | 12 | M | 4 | 00 |  |  | 2232384.docx
Gidgealpa Gas Satellite - Fuel Gas Supply - Fuel Gas Conditioning Skid | GIDG FUEL 1010-PCV-1224 | 1010-PCV-1224 | Regulator-Gas-GIDG_A019 | Ensure that regulator is installed in the correct orientat | 12 | M | 4 | 00 |  |  | 2232384.docx
Gidgealpa Gas Satellite - Fuel Gas Supply - Fuel Gas Conditioning Skid | GIDG FUEL 1010-PCV-1224 | 1010-PCV-1224 | Regulator-Gas-GIDG_A05 | Dismantle regulator and pilot | 12 | M | 4 | 00 |  |  | 2232384.docx
Gidgealpa Gas Satellite - Fuel Gas Supply - Fuel Gas Conditioning Skid | GIDG FUEL 1010-PCV-1224 | 1010-PCV-1224 | Regulator-Gas-GIDG_A013 | Check that components have not been damaged in transit or storage | 12 | M | 4 | 00 |  |  | 2232384.docx
Gidgealpa Gas Satellite - Fuel Gas Supply - Fuel Gas Conditioning Skid | GIDG FUEL 1010-PCV-1224 | 1010-PCV-1224 | Regulator-Gas-GIDG_A09 | Check condition of valve body clean if required | 12 | M | 4 | 00 |  |  | 2232384.docx
Gidgealpa Gas Satellite - Fuel Gas Supply - Fuel Gas Conditioning Skid | GIDG FUEL 1010-PCV-1224 | 1010-PCV-1224 | Regulator-Gas-GIDG_A08 | Check nozzle and seat replace if required | 12 | M | 4 | 00 |  |  | 2232384.docx
Gidgealpa Gas Satellite - Fuel Gas Supply - Fuel Gas Conditioning Skid | GIDG FUEL 1010-PCV-1224 | 1010-PCV-1224 | Regulator-Gas-GIDG_A016 | Ensure the gasket is of correct rating and size | 12 | M | 4 | 00 |  |  | 2232384.docx
Gidgealpa Gas Satellite - Fuel Gas Supply - Fuel Gas Conditioning Skid | GIDG FUEL 1010-PCV-1224 | 1010-PCV-1224 | Regulator-Gas-GIDG_A014 | Remove blanks and reinstall regulator into pipework | 12 | M | 4 | 00 |  |  | 2232384.docx
Gidgealpa Gas Satellite - Fuel Gas Supply - Fuel Gas Conditioning Skid | GIDG FUEL 1010-PCV-1224 | 1010-PCV-1224 | Regulator-Gas-GIDG_A017 | Remove pipe work supports | 12 | M | 4 | 00 |  |  | 2232384.docx
Gidgealpa Gas Satellite - Fuel Gas Supply - Fuel Gas Conditioning Skid | GIDG FUEL 1010-PCV-1224 | 1010-PCV-1224 | Regulator-Gas-GIDG_A06 | Inspect and replace any worn or damaged parts | 12 | M | 4 | 00 |  |  | 2232384.docx
Gidgealpa Gas Satellite - Fuel Gas Supply - Fuel Gas Conditioning Skid | GIDG FUEL 1010-PCV-1224 | 1010-PCV-1224 | Regulator-Gas-GIDG_A01 | Check that any tubing has been rubbing | 12 | M | 4 | 00 |  |  | 2232384.docx
Gidgealpa Gas Satellite - Fuel Gas Supply - Fuel Gas Conditioning Skid | GIDG FUEL 1010-PCV-1224 | 1010-PCV-1224 | Regulator-Gas-GIDG_A04 | Install blank flanges to pipe ends and tighten | 12 | M | 4 | 00 |  |  | 2232384.docx
Gidgealpa Gas Satellite - Fuel Gas Supply - Fuel Gas Conditioning Skid | GIDG FUEL 1010-PCV-1224 | 1010-PCV-1224 | Regulator-Gas-GIDG_A018 | Reconnect all instrumentation | 12 | M | 4 | 00 |  |  | 2232384.docx
Gidgealpa Gas Satellite - Fuel Gas Supply - Fuel Gas Conditioning Skid | GIDG FUEL 1010-PCV-1224 | 1010-PCV-1224 | Regulator-Gas-GIDG_A015 | Remove Blanks from Pipe Ends - take care as there may have been a build up of pressure | 12 | M | 4 | 00 |  |  | 2232384.docx
Gidgealpa Gas Satellite - Fuel Gas Supply - Fuel Gas Conditioning Skid | GIDG FUEL 1010-PCV-1224 | 1010-PCV-1224 | Regulator-Gas-GIDG_A010 | Inspect pilot valve and actuator for waxy residue, clean as reqired | 12 | M | 4 | 00 |  |  | 2232384.docx
Gidgealpa Gas Satellite - Fuel Gas Supply - Fuel Gas Conditioning Skid | GIDG FUEL 1010-PCV-1223 | 1010-PCV-1223 | Regulator-Gas-GIDG_A02 | Replace Support pipe | 12 | M | 4 | 00 |  |  | 2232384.docx
Gidgealpa Gas Satellite - Fuel Gas Supply - Fuel Gas Conditioning Skid | GIDG FUEL 1010-PCV-1223 | 1010-PCV-1223 | Regulator-Gas-GIDG_A05 | Dismantle regulator and pilot | 12 | M | 4 | 00 |  |  | 2232384.docx
Gidgealpa Gas Satellite - Fuel Gas Supply - Fuel Gas Conditioning Skid | GIDG FUEL 1010-PCV-1223 | 1010-PCV-1223 | Regulator-Gas-GIDG_A04 | Install blank flanges to pipe ends and tighten | 12 | M | 4 | 00 |  |  | 2232384.docx
Gidgealpa Gas Satellite - Fuel Gas Supply - Fuel Gas Conditioning Skid | GIDG FUEL 1010-PCV-1223 | 1010-PCV-1223 | Regulator-Gas-GIDG_A06 | Inspect and replace any worn or damaged parts | 12 | M | 4 | 00 |  |  | 2232384.docx
Gidgealpa Gas Satellite - Fuel Gas Supply - Fuel Gas Conditioning Skid | GIDG FUEL 1010-PCV-1223 | 1010-PCV-1223 | Regulator-Gas-GIDG_A015 | Remove Blanks from Pipe Ends - take care as there may have been a build up of pressure | 12 | M | 4 | 00 |  |  | 2232384.docx
Gidgealpa Gas Satellite - Fuel Gas Supply - Fuel Gas Conditioning Skid | GIDG FUEL 1010-PCV-1223 | 1010-PCV-1223 | Regulator-Gas-GIDG_A014 | Remove blanks and reinstall regulator into pipework | 12 | M | 4 | 00 |  |  | 2232384.docx
Gidgealpa Gas Satellite - Fuel Gas Supply - Fuel Gas Conditioning Skid | GIDG FUEL 1010-PCV-1223 | 1010-PCV-1223 | Regulator-Gas-GIDG_A09 | Check condition of valve body clean if required | 12 | M | 4 | 00 |  |  | 2232384.docx
Gidgealpa Gas Satellite - Fuel Gas Supply - Fuel Gas Conditioning Skid | GIDG FUEL 1010-PCV-1223 | 1010-PCV-1223 | Regulator-Gas-GIDG_A018 | Reconnect all instrumentation | 12 | M | 4 | 00 |  |  | 2232384.docx
Gidgealpa Gas Satellite - Fuel Gas Supply - Fuel Gas Conditioning Skid | GIDG FUEL 1010-PCV-1223 | 1010-PCV-1223 | Regulator-Gas-GIDG_A07 | Check condition of seals | 12 | M | 4 | 00 |  |  | 2232384.docx
Gidgealpa Gas Satellite - Fuel Gas Supply - Fuel Gas Conditioning Skid | GIDG FUEL 1010-PCV-1223 | 1010-PCV-1223 | Regulator-Gas-GIDG_A08 | Check nozzle and seat replace if required | 12 | M | 4 | 00 |  |  | 2232384.docx
Gidgealpa Gas Satellite - Fuel Gas Supply - Fuel Gas Conditioning Skid | GIDG FUEL 1010-PCV-1223 | 1010-PCV-1223 | Regulator-Gas-GIDG_A019 | Ensure that regulator is installed in the correct orientat | 12 | M | 4 | 00 |  |  | 2232384.docx
Gidgealpa Gas Satellite - Fuel Gas Supply - Fuel Gas Conditioning Skid | GIDG FUEL 1010-PCV-1223 | 1010-PCV-1223 | Regulator-Gas-GIDG_A01 | Check that any tubing has been rubbing | 12 | M | 4 | 00 |  |  | 2232384.docx
Gidgealpa Gas Satellite - Fuel Gas Supply - Fuel Gas Conditioning Skid | GIDG FUEL 1010-PCV-1223 | 1010-PCV-1223 | Regulator-Gas-GIDG_A017 | Remove pipe work supports | 12 | M | 4 | 00 |  |  | 2232384.docx
Gidgealpa Gas Satellite - Fuel Gas Supply - Fuel Gas Conditioning Skid | GIDG FUEL 1010-PCV-1223 | 1010-PCV-1223 | Regulator-Gas-GIDG_A03 | Check Gramaphone on Flange faces before installing blank flange | 12 | M | 4 | 00 |  |  | 2232384.docx
Gidgealpa Gas Satellite - Fuel Gas Supply - Fuel Gas Conditioning Skid | GIDG FUEL 1010-PCV-1223 | 1010-PCV-1223 | Regulator-Gas-GIDG_A013 | Check that components have not been damaged in transit or storage | 12 | M | 4 | 00 |  |  | 2232384.docx
Gidgealpa Gas Satellite - Fuel Gas Supply - Fuel Gas Conditioning Skid | GIDG FUEL 1010-PCV-1223 | 1010-PCV-1223 | Regulator-Gas-GIDG_A016 | Ensure the gasket is of correct rating and size | 12 | M | 4 | 00 |  |  | 2232384.docx
Gidgealpa Gas Satellite - Fuel Gas Supply - Fuel Gas Conditioning Skid | GIDG FUEL 1010-PCV-1223 | 1010-PCV-1223 | Regulator-Gas-GIDG_A010 | Inspect pilot valve and actuator for waxy residue, clean as reqired | 12 | M | 4 | 00 |  |  | 2232384.docx
Gidgealpa Gas Satellite - Fuel Gas Supply - Fuel Gas Conditioning Skid | GIDG FUEL 1010-PCV-1223 | 1010-PCV-1223 | Regulator-Gas-GIDG_A012 | Ensure that all components are clean and free of contaminants | 12 | M | 4 | 00 |  |  | 2232384.docx
Gidgealpa Gas Satellite - Fuel Gas Supply - Fuel Gas Conditioning Skid | GIDG FUEL 1010-PCV-1223 | 1010-PCV-1223 | Regulator-Gas-GIDG_A011 | Reassemble regulator and pilot | 12 | M | 4 | 00 |  |  | 2232384.docx
Gidgealpa Gas Satellite - Fuel Gas Supply - Fuel Gas Conditioning Skid | GIDG FUEL 1010-PCV-1212 | 1010-PCV-1212 | Regulator-Gas-GIDG_A011 | Reassemble regulator and pilot | 12 | M | 4 | 00 |  |  | 2232384.docx | 001
Gidgealpa Gas Satellite - Fuel Gas Supply - Fuel Gas Conditioning Skid | GIDG FUEL 1010-PCV-1212 | 1010-PCV-1212 | Regulator-Gas-GIDG_A02 | Replace Support pipe | 12 | M | 4 | 00 |  |  | 2232384.docx
Gidgealpa Gas Satellite - Fuel Gas Supply - Fuel Gas Conditioning Skid | GIDG FUEL 1010-PCV-1212 | 1010-PCV-1212 | Regulator-Gas-GIDG_A012 | Ensure that all components are clean and free of contaminants | 12 | M | 4 | 00 |  |  | 2232384.docx
Gidgealpa Gas Satellite - Fuel Gas Supply - Fuel Gas Conditioning Skid | GIDG FUEL 1010-PCV-1212 | 1010-PCV-1212 | Regulator-Gas-GIDG_A07 | Check condition of seals | 12 | M | 4 | 00 |  |  | 2232384.docx
Gidgealpa Gas Satellite - Fuel Gas Supply - Fuel Gas Conditioning Skid | GIDG FUEL 1010-PCV-1212 | 1010-PCV-1212 | Regulator-Gas-GIDG_A03 | Check Gramaphone on Flange faces before installing blank flange | 12 | M | 4 | 00 |  |  | 2232384.docx
Gidgealpa Gas Satellite - Fuel Gas Supply - Fuel Gas Conditioning Skid | GIDG FUEL 1010-PCV-1212 | 1010-PCV-1212 | Regulator-Gas-GIDG_A019 | Ensure that regulator is installed in the correct orientat | 12 | M | 4 | 00 |  |  | 2232384.docx
Gidgealpa Gas Satellite - Fuel Gas Supply - Fuel Gas Conditioning Skid | GIDG FUEL 1010-PCV-1212 | 1010-PCV-1212 | Regulator-Gas-GIDG_A05 | Dismantle regulator and pilot | 12 | M | 4 | 00 |  |  | 2232384.docx
Gidgealpa Gas Satellite - Fuel Gas Supply - Fuel Gas Conditioning Skid | GIDG FUEL 1010-PCV-1212 | 1010-PCV-1212 | Regulator-Gas-GIDG_A013 | Check that components have not been damaged in transit or storage | 12 | M | 4 | 00 |  |  | 2232384.docx
Gidgealpa Gas Satellite - Fuel Gas Supply - Fuel Gas Conditioning Skid | GIDG FUEL 1010-PCV-1212 | 1010-PCV-1212 | Regulator-Gas-GIDG_A09 | Check condition of valve body clean if required | 12 | M | 4 | 00 |  |  | 2232384.docx | 001
Gidgealpa Gas Satellite - Fuel Gas Supply - Fuel Gas Conditioning Skid | GIDG FUEL 1010-PCV-1212 | 1010-PCV-1212 | Regulator-Gas-GIDG_A08 | Check nozzle and seat replace if required | 12 | M | 4 | 00 |  |  | 2232384.docx
Gidgealpa Gas Satellite - Fuel Gas Supply - Fuel Gas Conditioning Skid | GIDG FUEL 1010-PCV-1212 | 1010-PCV-1212 | Regulator-Gas-GIDG_A016 | Ensure the gasket is of correct rating and size | 12 | M | 4 | 00 |  |  | 2232384.docx
Gidgealpa Gas Satellite - Fuel Gas Supply - Fuel Gas Conditioning Skid | GIDG FUEL 1010-PCV-1212 | 1010-PCV-1212 | Regulator-Gas-GIDG_A014 | Remove blanks and reinstall regulator into pipework | 12 | M | 4 | 00 |  |  | 2232384.docx
Gidgealpa Gas Satellite - Fuel Gas Supply - Fuel Gas Conditioning Skid | GIDG FUEL 1010-PCV-1212 | 1010-PCV-1212 | Regulator-Gas-GIDG_A017 | Remove pipe work supports | 12 | M | 4 | 00 |  |  | 2232384.docx
Gidgealpa Gas Satellite - Fuel Gas Supply - Fuel Gas Conditioning Skid | GIDG FUEL 1010-PCV-1212 | 1010-PCV-1212 | Regulator-Gas-GIDG_A06 | Inspect and replace any worn or damaged parts | 12 | M | 4 | 00 |  |  | 2232384.docx
Gidgealpa Gas Satellite - Fuel Gas Supply - Fuel Gas Conditioning Skid | GIDG FUEL 1010-PCV-1212 | 1010-PCV-1212 | Regulator-Gas-GIDG_A01 | Check that any tubing has been rubbing | 12 | M | 4 | 00 |  |  | 2232384.docx
Gidgealpa Gas Satellite - Fuel Gas Supply - Fuel Gas Conditioning Skid | GIDG FUEL 1010-PCV-1212 | 1010-PCV-1212 | Regulator-Gas-GIDG_A04 | Install blank flanges to pipe ends and tighten | 12 | M | 4 | 00 |  |  | 2232384.docx
Gidgealpa Gas Satellite - Fuel Gas Supply - Fuel Gas Conditioning Skid | GIDG FUEL 1010-PCV-1212 | 1010-PCV-1212 | Regulator-Gas-GIDG_A018 | Reconnect all instrumentation | 12 | M | 4 | 00 |  |  | 2232384.docx
Gidgealpa Gas Satellite - Fuel Gas Supply - Fuel Gas Conditioning Skid | GIDG FUEL 1010-PCV-1212 | 1010-PCV-1212 | Regulator-Gas-GIDG_A015 | Remove Blanks from Pipe Ends - take care as there may have been a build up of pressure | 12 | M | 4 | 00 |  |  | 2232384.docx
Gidgealpa Gas Satellite - Fuel Gas Supply - Fuel Gas Conditioning Skid | GIDG FUEL 1010-PCV-1212 | 1010-PCV-1212 | Regulator-Gas-GIDG_A010 | Inspect pilot valve and actuator for waxy residue, clean as reqired | 12 | M | 4 | 00 |  |  | 2232384.docx
Gidgealpa Gas Satellite - Fuel Gas Supply - Fuel Gas Conditioning Skid | GIDG FUEL 1010-PCV-1211 | 1010-PCV-1211 | Regulator-Gas-GIDG_A05 | Dismantle regulator and pilot | 12 | M | 4 | 00 |  |  | 2232384.docx
Gidgealpa Gas Satellite - Fuel Gas Supply - Fuel Gas Conditioning Skid | GIDG FUEL 1010-PCV-1211 | 1010-PCV-1211 | Regulator-Gas-GIDG_A02 | Replace Support pipe | 12 | M | 4 | 00 |  |  | 2232384.docx
Gidgealpa Gas Satellite - Fuel Gas Supply - Fuel Gas Conditioning Skid | GIDG FUEL 1010-PCV-1211 | 1010-PCV-1211 | Regulator-Gas-GIDG_A04 | Install blank flanges to pipe ends and tighten | 12 | M | 4 | 00 |  |  | 2232384.docx
Gidgealpa Gas Satellite - Fuel Gas Supply - Fuel Gas Conditioning Skid | GIDG FUEL 1010-PCV-1211 | 1010-PCV-1211 | Regulator-Gas-GIDG_A06 | Inspect and replace any worn or damaged parts | 12 | M | 4 | 00 |  |  | 2232384.docx
Gidgealpa Gas Satellite - Fuel Gas Supply - Fuel Gas Conditioning Skid | GIDG FUEL 1010-PCV-1211 | 1010-PCV-1211 | Regulator-Gas-GIDG_A015 | Remove Blanks from Pipe Ends - take care as there may have been a build up of pressure | 12 | M | 4 | 00 |  |  | 2232384.docx
Gidgealpa Gas Satellite - Fuel Gas Supply - Fuel Gas Conditioning Skid | GIDG FUEL 1010-PCV-1211 | 1010-PCV-1211 | Regulator-Gas-GIDG_A014 | Remove blanks and reinstall regulator into pipework | 12 | M | 4 | 00 |  |  | 2232384.docx
Gidgealpa Gas Satellite - Fuel Gas Supply - Fuel Gas Conditioning Skid | GIDG FUEL 1010-PCV-1211 | 1010-PCV-1211 | Regulator-Gas-GIDG_A09 | Check condition of valve body clean if required | 12 | M | 4 | 00 |  |  | 2232384.docx
Gidgealpa Gas Satellite - Fuel Gas Supply - Fuel Gas Conditioning Skid | GIDG FUEL 1010-PCV-1211 | 1010-PCV-1211 | Regulator-Gas-GIDG_A018 | Reconnect all instrumentation | 12 | M | 4 | 00 |  |  | 2232384.docx
Gidgealpa Gas Satellite - Fuel Gas Supply - Fuel Gas Conditioning Skid | GIDG FUEL 1010-PCV-1211 | 1010-PCV-1211 | Regulator-Gas-GIDG_A07 | Check condition of seals | 12 | M | 4 | 00 |  |  | 2232384.docx | 001
Gidgealpa Gas Satellite - Fuel Gas Supply - Fuel Gas Conditioning Skid | GIDG FUEL 1010-PCV-1211 | 1010-PCV-1211 | Regulator-Gas-GIDG_A08 | Check nozzle and seat replace if required | 12 | M | 4 | 00 |  |  | 2232384.docx
Gidgealpa Gas Satellite - Fuel Gas Supply - Fuel Gas Conditioning Skid | GIDG FUEL 1010-PCV-1211 | 1010-PCV-1211 | Regulator-Gas-GIDG_A019 | Ensure that regulator is installed in the correct orientat | 12 | M | 4 | 00 |  |  | 2232384.docx | 001
Gidgealpa Gas Satellite - Fuel Gas Supply - Fuel Gas Conditioning Skid | GIDG FUEL 1010-PCV-1211 | 1010-PCV-1211 | Regulator-Gas-GIDG_A01 | Check that any tubing has been rubbing | 12 | M | 4 | 00 |  |  | 2232384.docx
Gidgealpa Gas Satellite - Fuel Gas Supply - Fuel Gas Conditioning Skid | GIDG FUEL 1010-PCV-1211 | 1010-PCV-1211 | Regulator-Gas-GIDG_A017 | Remove pipe work supports | 12 | M | 4 | 00 |  |  | 2232384.docx | 001
Gidgealpa Gas Satellite - Fuel Gas Supply - Fuel Gas Conditioning Skid | GIDG FUEL 1010-PCV-1211 | 1010-PCV-1211 | Regulator-Gas-GIDG_A03 | Check Gramaphone on Flange faces before installing blank flange | 12 | M | 4 | 00 |  |  | 2232384.docx
Gidgealpa Gas Satellite - Fuel Gas Supply - Fuel Gas Conditioning Skid | GIDG FUEL 1010-PCV-1211 | 1010-PCV-1211 | Regulator-Gas-GIDG_A013 | Check that components have not been damaged in transit or storage | 12 | M | 4 | 00 |  |  | 2232384.docx | 001
Gidgealpa Gas Satellite - Fuel Gas Supply - Fuel Gas Conditioning Skid | GIDG FUEL 1010-PCV-1211 | 1010-PCV-1211 | Regulator-Gas-GIDG_A016 | Ensure the gasket is of correct rating and size | 12 | M | 4 | 00 |  |  | 2232384.docx | 001
Gidgealpa Gas Satellite - Fuel Gas Supply - Fuel Gas Conditioning Skid | GIDG FUEL 1010-PCV-1211 | 1010-PCV-1211 | Regulator-Gas-GIDG_A010 | Inspect pilot valve and actuator for waxy residue, clean as reqired | 12 | M | 4 | 00 |  |  | 2232384.docx
Gidgealpa Gas Satellite - Fuel Gas Supply - Fuel Gas Conditioning Skid | GIDG FUEL 1010-PCV-1211 | 1010-PCV-1211 | Regulator-Gas-GIDG_A012 | Ensure that all components are clean and free of contaminants | 12 | M | 4 | 00 |  |  | 2232384.docx
Gidgealpa Gas Satellite - Inlet Separation - Gathering Manifold | GIDG INL SEP 115287-GE-0001 | 115287-GE-0001 | Engine-Compressor-GIDG_A020 | Check / Clean Engine Start Gas Y-Strainers (If Fitted) | 6 | M | 4 | 00 |  |  | 0001-296-TIN-0058.pdf | 001
Gidgealpa Gas Satellite - Inlet Separation - Gathering Manifold | GIDG INL SEP 115287-KX-0001 | 115287-KX-0001 | Compressor Package IE-Screw-GIDG_A09 | Inspect & Calibrate Discharge Header Multivariable Transmitter | 1 | Y | 01 | 00 |  |  | 0001-295-TIN-0021.pdf | 001
Gidgealpa Gas Satellite - Inlet Separation - Gathering Manifold | GIDG INL SEP 115287-KX-0001 | 115287-KX-0001 | Compressor Package IE-Screw-GIDG_A28 | Inspect & Calibrate Engine Oil Pressure Transmitter | 1 | Y | 01 | 00 |  |  | 0001-295-TIN-0021.pdf
Gidgealpa Gas Satellite - Inlet Separation - Gathering Manifold | GIDG INL SEP 115287-KX-0001 | 115287-KX-0001 | Compressor Package IE-Screw-GIDG_A37 | Inspect & Calibrate Fuel Gas Scrubber Level Controller | 1 | Y | 01 | 00 |  |  | 0001-295-TIN-0021.pdf
Gidgealpa Gas Satellite - Inlet Separation - Gathering Manifold | GIDG INL SEP 115287-KX-0001 | 115287-KX-0001 | Compressor Package IE-Screw-GIDG_A12 | Inspect & Calibrate Compressor Slide Valve Position Transmitter | 1 | Y | 01 | 00 |  |  | 0001-295-TIN-0021.pdf
Gidgealpa Gas Satellite - Inlet Separation - Gathering Manifold | GIDG INL SEP 115287-KX-0001 | 115287-KX-0001 | Compressor Package IE-Screw-GIDG_A27 | Inspect & Calibrate Control Panel Temperature Element | 1 | Y | 01 | 00 |  |  | 0001-295-TIN-0021.pdf
Gidgealpa Gas Satellite - Inlet Separation - Gathering Manifold | GIDG INL SEP 115287-KX-0001 | 115287-KX-0001 | Compressor Package IE-Screw-GIDG_A14 | Inspect & Calibrate Discharge Temperature Element | 1 | Y | 01 | 00 |  |  | 0001-295-TIN-0021.pdf | 001
Gidgealpa Gas Satellite - Inlet Separation - Gathering Manifold | GIDG INL SEP 115287-KX-0001 | 115287-KX-0001 | Compressor Package IE-Screw-GIDG_A05 | Inspect & Calibrate Inlet Separator Pressure Transmitter | 1 | Y | 01 | 00 |  |  | 0001-295-TIN-0021.pdf
Gidgealpa Gas Satellite - Inlet Separation - Gathering Manifold | GIDG INL SEP 115287-KX-0001 | 115287-KX-0001 | Compressor Package IE-Screw-GIDG_A13 | Inspect & Calibrate Discharge Pressure Transmitter | 1 | Y | 01 | 00 |  |  | 0001-295-TIN-0021.pdf
Gidgealpa Gas Satellite - Inlet Separation - Gathering Manifold | GIDG INL SEP 115287-KX-0001 | 115287-KX-0001 | Compressor Package IE-Screw-GIDG_A11 | Inspect & Calibrate Casing Vibration Transmitter | 1 | Y | 01 | 00 |  |  | 0001-295-TIN-0021.pdf
Gidgealpa Gas Satellite - Inlet Separation - Gathering Manifold | GIDG INL SEP 115287-KX-0001 | 115287-KX-0001 | Compressor Package IE-Screw-GIDG_A26 | Inspect & Calibrate Oil Moisture Analyser | 1 | Y | 01 | 00 |  |  | 0001-295-TIN-0021.pdf
Gidgealpa Gas Satellite - Inlet Separation - Gathering Manifold | GIDG INL SEP 115287-KX-0001 | 115287-KX-0001 | Compressor Package IE-Screw-GIDG_A38 | Inspect & Calibrate Fuel Gas Pressure Transmitter | 1 | Y | 01 | 00 |  |  | 0001-295-TIN-0021.pdf
Gidgealpa Gas Satellite - Inlet Separation - Gathering Manifold | GIDG INL SEP 115287-KX-0001 | 115287-KX-0001 | Compressor Package IE-Screw-GIDG_A01 | Inspect & Calibrate Package Suction Pressure Transmitter | 1 | Y | 01 | 00 |  |  | 0001-295-TIN-0021.pdf
Gidgealpa Gas Satellite - Inlet Separation - Gathering Manifold | GIDG INL SEP 115287-KX-0001 | 115287-KX-0001 | Compressor Package IE-Screw-GIDG_A15 | Inspect & Calibrate Discharge Scrubber Level Transmitter | 1 | Y | 01 | 00 |  |  | 0001-295-TIN-0021.pdf
Gidgealpa Gas Satellite - Inlet Separation - Gathering Manifold | GIDG INL SEP 115287-KX-0001 | 115287-KX-0001 | Compressor Package IE-Screw-GIDG_A33 | Inspect & Calibrate Engine Speed | 1 | Y | 01 | 00 |  |  | 0001-295-TIN-0021.pdf
Gidgealpa Gas Satellite - Inlet Separation - Gathering Manifold | GIDG INL SEP 115287-KX-0001 | 115287-KX-0001 | Compressor Package IE-Screw-GIDG_A10 | Inspect & Calibrate Suction Temperature Element | 1 | Y | 01 | 00 |  |  | 0001-295-TIN-0021.pdf
Gidgealpa Gas Satellite - Inlet Separation - Gathering Manifold | GIDG INL SEP 115287-KX-0001 | 115287-KX-0001 | Compressor Package IE-Screw-GIDG_A24 | Inspect & Calibrate Aux Surge Tank Low Level Switch | 1 | Y | 01 | 00 |  |  | 0001-295-TIN-0021.pdf | 001
Gidgealpa Gas Satellite - Inlet Separation - Gathering Manifold | GIDG INL SEP 115287-KX-0001 | 115287-KX-0001 | Compressor Package IE-Screw-GIDG_A06 | Inspect & Calibrate Blowcase Level Transmitter | 1 | Y | 01 | 00 |  |  | 0001-295-TIN-0021.pdf | 001
Gidgealpa Gas Satellite - Inlet Separation - Gathering Manifold | GIDG INL SEP 115287-KX-0001 | 115287-KX-0001 | Compressor Package IE-Screw-GIDG_A07 | Inspect & Calibrate Discharge Header Pressure Transmitter | 1 | Y | 01 | 00 |  |  | 0001-295-TIN-0021.pdf
Gidgealpa Gas Satellite - Inlet Separation - Gathering Manifold | GIDG INL SEP 115287-KX-0001 | 115287-KX-0001 | Compressor Package IE-Screw-GIDG_A17 | Inspect & Calibrate Discharge Scrubber Low Level Switch | 1 | Y | 01 | 00 |  |  | 0001-295-TIN-0021.pdf
Gidgealpa Gas Satellite - Inlet Separation - Gathering Manifold | GIDG INL SEP 115287-KX-0001 | 115287-KX-0001 | Compressor Package IE-Screw-GIDG_A19 | Inspect & Calibrate Discharge Header Temperature Element | 1 | Y | 01 | 00 |  |  | 0001-295-TIN-0021.pdf
Gidgealpa Gas Satellite - Inlet Separation - Gathering Manifold | GIDG INL SEP 115287-KX-0001 | 115287-KX-0001 | Compressor Package IE-Screw-GIDG_A18 | Inspect & Calibrate Discharge Scrubber Temperature Element | 1 | Y | 01 | 00 |  |  | 0001-295-TIN-0021.pdf
Gidgealpa Gas Satellite - Inlet Separation - Gathering Manifold | GIDG INL SEP 115287-KX-0001 | 115287-KX-0001 | Compressor Package IE-Screw-GIDG_A35 | Inspect & Calibrate Engine Oil Low Level | 1 | Y | 01 | 00 |  |  | 0001-295-TIN-0021.pdf
Gidgealpa Gas Satellite - Inlet Separation - Gathering Manifold | GIDG INL SEP 115287-KX-0001 | 115287-KX-0001 | Compressor Package IE-Screw-GIDG_A08 | Inspect & Calibrate Discharge Pressure Control Valve Positioner | 1 | Y | 01 | 00 |  |  | 0001-295-TIN-0021.pdf
Gidgealpa Gas Satellite - Inlet Separation - Gathering Manifold | GIDG INL SEP 115287-KX-0001 | 115287-KX-0001 | Compressor Package IE-Screw-GIDG_A25 | Inspect & Calibrate Air Cooler Vibration Transmitter | 1 | Y | 01 | 00 |  |  | 0001-295-TIN-0021.pdf
Gidgealpa Gas Satellite - Inlet Separation - Gathering Manifold | GIDG INL SEP 115287-KX-0001 | 115287-KX-0001 | Compressor Package IE-Screw-GIDG_A23 | Inspect & Calibrate JW Surge Tank Low Level Switch | 1 | Y | 01 | 00 |  |  | 0001-295-TIN-0021.pdf | 001
Gidgealpa Gas Satellite - Inlet Separation - Gathering Manifold | GIDG INL SEP 115287-KX-0001 | 115287-KX-0001 | Compressor Package IE-Screw-GIDG_A30 | Inspect & Calibrate Engine Oil Temperature Sensor | 1 | Y | 01 | 00 |  |  | 0001-295-TIN-0021.pdf | 001
Gidgealpa Gas Satellite - Inlet Separation - Gathering Manifold | GIDG INL SEP 115287-KX-0001 | 115287-KX-0001 | Compressor Package IE-Screw-GIDG_A16 | Inspect & Calibrate Discharge Scrubber High Level Switch | 1 | Y | 01 | 00 |  |  | 0001-295-TIN-0021.pdf
Gidgealpa Gas Satellite - Inlet Separation - Gathering Manifold | GIDG INL SEP 115287-KX-0001 | 115287-KX-0001 | Compressor Package IE-Screw-GIDG_A04 | Inspect & Calibrate Inlet Separator High Level Switch | 1 | Y | 01 | 00 |  |  | 0001-295-TIN-0021.pdf
Gidgealpa Gas Satellite - Inlet Separation - Gathering Manifold | GIDG INL SEP 115287-KX-0001 | 115287-KX-0001 | Compressor Package IE-Screw-GIDG_A36 | Inspect & Calibrate Fuel Gas Scrubber High Level Switch | 1 | Y | 01 | 00 |  |  | 0001-295-TIN-0021.pdf
Gidgealpa Gas Satellite - Inlet Separation - Gathering Manifold | GIDG INL SEP 115287-KX-0001 | 115287-KX-0001 | Compressor Package IE-Screw-GIDG_A32 | Inspect & Calibrate MT Temperature Sensor | 1 | Y | 01 | 00 |  |  | 0001-295-TIN-0021.pdf
Gidgealpa Gas Satellite - Inlet Separation - Gathering Manifold | GIDG INL SEP 115287-KX-0001 | 115287-KX-0001 | Compressor Package IE-Screw-GIDG_A03 | Inspect & Calibrate Inlet Separator Level Transmitter | 1 | Y | 01 | 00 |  |  | 0001-295-TIN-0021.pdf | 001
Gidgealpa Gas Satellite - Inlet Separation - Gathering Manifold | GIDG INL SEP 115287-KX-0001 | 115287-KX-0001 | Compressor Package IE-Screw-GIDG_A22 | Inspect & Calibrate Glycol Circuit Pressure Transmitter | 1 | Y | 01 | 00 |  |  | 0001-295-TIN-0021.pdf
Gidgealpa Gas Satellite - Inlet Separation - Gathering Manifold | GIDG INL SEP 115287-KX-0001 | 115287-KX-0001 | Compressor Package IE-Screw-GIDG_A02 | Inspect & Calibrate Suction Pressure Control Valve Positioner | 1 | Y | 01 | 00 |  |  | 0001-295-TIN-0021.pdf
Gidgealpa Gas Satellite - Inlet Separation - Gathering Manifold | GIDG INL SEP 115287-KX-0001 | 115287-KX-0001 | Compressor Package IE-Screw-GIDG_A21 | Inspect & Calibrate Bearing Oil Pressure Transmitter | 1 | Y | 01 | 00 |  |  | 0001-295-TIN-0021.pdf
Gidgealpa Gas Satellite - Inlet Separation - Gathering Manifold | GIDG INL SEP 115287-KX-0001 | 115287-KX-0001 | Compressor Package IE-Screw-GIDG_A31 | Inspect & Calibrate Jacket Water Temperature Sensor | 1 | Y | 01 | 00 |  |  | 0001-295-TIN-0021.pdf
Gidgealpa Gas Satellite - Inlet Separation - Gathering Manifold | GIDG INL SEP 115287-KX-0001 | 115287-KX-0001 | Compressor Package IE-Screw-GIDG_A29 | Inspect & Calibrate Engine Vibration Transmitter | 1 | Y | 01 | 00 |  |  | 0001-295-TIN-0021.pdf
Gidgealpa Gas Satellite - Inlet Separation - Gathering Manifold | GIDG INL SEP 115287-KX-0001 | 115287-KX-0001 | Compressor Package IE-Screw-GIDG_A20 | Inspect & Calibrate Bearing Oil Temperature Element | 1 | Y | 01 | 00 |  |  | 0001-295-TIN-0021.pdf
Gidgealpa Gas Satellite - Inlet Separation - Gathering Manifold | GIDG INL SEP 115287-K-0001 | 115287-K-0001 | Compressor-Screw-GIDG_A06 | INSPECT / CLEAN VENTS / DRAINS | 6 | W | 4 | 00 |  |  | 0001-296-TIN-0041.pdf
Gidgealpa Gas Satellite - Inlet Separation - Gathering Manifold | GIDG INL SEP 115287-K-0001 | 115287-K-0001 | Compressor-Screw-GIDG_A01 | INSPECT (WALK AROUND) ENGINE / COMPRESSOR PACKAGE | 6 | W | 4 | 01 |  |  | 0001-296-TIN-0041.pdf
Gidgealpa Gas Satellite - Inlet Separation - Gathering Manifold | GIDG INL SEP 115287-K-0001 | 115287-K-0001 | Compressor-Screw-GIDG_A02 | INSPECT SUCTION / DISCHARGE FLANGES | 6 | W | 4 | 01 |  |  | 0001-296-TIN-0041.pdf
Gidgealpa Gas Satellite - Inlet Separation - Gathering Manifold | GIDG INL SEP 115287-K-0001 | 115287-K-0001 | Compressor-Screw-GIDG_A05 | CHECK / RECORD SUCTION STRAINER | 6 | W | 4 | 00 |  |  | 0001-296-TIN-0041.pdf | 001
Gidgealpa Gas Satellite - Inlet Separation - Gathering Manifold | GIDG INL SEP 115287-K-0001 | 115287-K-0001 | Compressor-Screw-GIDG_A09 | CHECK / ADJUST SUCTION / DISCHARGE FLANGE BOLTS | 6 | M | 4 | 00 |  |  | 0001-296-TIN-0042.pdf | 001
Gidgealpa Gas Satellite - Inlet Separation - Gathering Manifold | GIDG INL SEP 115287-K-0001 | 115287-K-0001 | Compressor-Screw-GIDG_A011 | INSPECT / ADJUST ALIGNMENT | 1 | Y | 4 | 00 |  |  | 0001-296-TIN-0027.pdf
Gidgealpa Gas Satellite - Inlet Separation - Gathering Manifold | GIDG INL SEP 115287-K-0001 | 115287-K-0001 | Compressor-Screw-GIDG_A08 | INSPECT / REPLACE COUPLING | 6 | M | 4 | 00 |  |  | 0001-296-TIN-0042.pdf | 001
Gidgealpa Gas Satellite - Inlet Separation - Gathering Manifold | GIDG INL SEP 115287-K-0001 | 115287-K-0001 | Compressor-Screw-GIDG_A010 | CHECK / TENSION MOUNTING FASTENERS | 6 | M | 4 | 00 |  |  | 0001-296-TIN-0042.pdf
Gidgealpa Gas Satellite - Inlet Separation - Gathering Manifold | GIDG INL SEP 115287-K-0001 | 115287-K-0001 | Compressor-Screw-GIDG_A07 | CHECK / CLEAN LUBE OIL Y-STRAINER | 6 | M | 4 | 00 |  |  | 0001-296-TIN-0042.pdf
Gidgealpa Gas Satellite - Inlet Separation - Gathering Manifold | GIDG INL SEP 115287-K-0001 | 115287-K-0001 | Compressor-Screw-GIDG_A04 | REPLACE FILTERS | 6 | W | 4 | 00 |  |  | 0001-296-TIN-0041.pdf
Gidgealpa Gas Satellite - Inlet Separation - Gathering Manifold | GIDG INL SEP 115287-K-0001 | 115287-K-0001 | Compressor-Screw-GIDG_A03 | CHECK COMPRESSOR OIL LEVEL | 6 | W | 4 | 01 |  |  | 0001-296-TIN-0041.pdf | 001
Gidgealpa Gas Satellite - Inlet Separation - Gathering Manifold | GIDG INL SEP 115287-GE-0001 | 115287-GE-0001 | Engine-Compressor-GIDG_A054 | Check / Record Cylinder liners, while heads are removed | 3 | Y | 4 | 00 |  |  | 0001-296-TIN-0058.pdf
Gidgealpa Gas Satellite - Inlet Separation - Gathering Manifold | GIDG INL SEP 115287-GE-0001 | 115287-GE-0001 | Engine-Compressor-GIDG_A035 | Check / Record Cylinder Compression | 1 | Y | 4 | 00 |  |  | 0001-296-TIN-0058.pdf
Gidgealpa Gas Satellite - Inlet Separation - Gathering Manifold | GIDG INL SEP 115287-GE-0001 | 115287-GE-0001 | Engine-Compressor-GIDG_A056 | Replace Cylinder Head | 3 | Y | 4 | 00 |  |  | 0001-296-TIN-0058.pdf | 001
Gidgealpa Gas Satellite - Inlet Separation - Gathering Manifold | GIDG INL SEP 115287-GE-0001 | 115287-GE-0001 | Engine-Compressor-GIDG_A051 | Replace Gas 'A' Regulator Diaphragms and Filters | 3 | Y | 4 | 00 |  |  | 0001-296-TIN-0058.pdf
Gidgealpa Gas Satellite - Inlet Separation - Gathering Manifold | GIDG INL SEP 115287-GE-0001 | 115287-GE-0001 | Engine-Compressor-GIDG_A02 | Check / Record Fuel Gas Filter Differential Pressure | 6 | W | 4 | 00 |  |  | 0001-296-TIN-0058.pdf
Gidgealpa Gas Satellite - Inlet Separation - Gathering Manifold | GIDG INL SEP 115287-GE-0001 | 115287-GE-0001 | Engine-Compressor-GIDG_A027 | Replace Air Cleaner Primary Filter Element | 6 | M | 4 | 00 |  |  | 0001-296-TIN-0058.pdf
Gidgealpa Gas Satellite - Inlet Separation - Gathering Manifold | GIDG INL SEP 115287-GE-0001 | 115287-GE-0001 | Engine-Compressor-GIDG_A011 | Check / Adjust Fuel Gas Supply Pressure Regulator | 6 | W | 4 | 00 |  |  | 0001-296-TIN-0058.pdf
Gidgealpa Gas Satellite - Inlet Separation - Gathering Manifold | GIDG INL SEP 115287-GE-0001 | 115287-GE-0001 | Engine-Compressor-GIDG_A012 | Check / Adjust Carburettor , O2%, NOx emission, gas over air. | 6 | W | 4 | 00 |  |  | 0001-296-TIN-0058.pdf | 001
Gidgealpa Gas Satellite - Inlet Separation - Gathering Manifold | GIDG INL SEP 115287-GE-0001 | 115287-GE-0001 | Engine-Compressor-GIDG_A024 | CheckInlet Air System, Ducting, Rubber Elbows / Connectors, Clamps | 6 | M | 4 | 00 |  |  | 0001-296-TIN-0058.pdf | 001
Gidgealpa Gas Satellite - Inlet Separation - Gathering Manifold | GIDG INL SEP 115287-GE-0001 | 115287-GE-0001 | Engine-Compressor-GIDG_A014 | Check / Clean Air Filter Pre-Cleaner | 6 | W | 4 | 00 |  |  | 0001-296-TIN-0058.pdf
Gidgealpa Gas Satellite - Inlet Separation - Gathering Manifold | GIDG INL SEP 115287-GE-0001 | 115287-GE-0001 | Engine-Compressor-GIDG_A070 | Check Fuel Gas and Start Gas Supply Lines / System | 6 | Y | 4 | 00 |  |  | 0001-296-TIN-0058.pdf
Gidgealpa Gas Satellite - Inlet Separation - Gathering Manifold | GIDG INL SEP 115287-GE-0001 | 115287-GE-0001 | Engine-Compressor-GIDG_A074 | Replace Inlet Air System, Ducting, Rubber Elbows / Connectors,Clamps | 6 | Y | 4 | 00 |  |  | 0001-296-TIN-0058.pdf
Gidgealpa Gas Satellite - Inlet Separation - Gathering Manifold | GIDG INL SEP 115287-GE-0001 | 115287-GE-0001 | Engine-Compressor-GIDG_A042 | Replace Fuel Gas Filter Element (Skid) | 1 | Y | 4 | 00 |  |  | 0001-296-TIN-0058.pdf
Gidgealpa Gas Satellite - Inlet Separation - Gathering Manifold | GIDG INL SEP 115287-GE-0001 | 115287-GE-0001 | Engine-Compressor-GIDG_A043 | Check / Replace Air Cleaner Secondary Filter Element | 1 | Y | 4 | 00 |  |  | 0001-296-TIN-0058.pdf
Gidgealpa Gas Satellite - Inlet Separation - Gathering Manifold | GIDG INL SEP 115287-GE-0001 | 115287-GE-0001 | Engine-Compressor-GIDG_A065 | Replace Main Fuel Gas Supply Pressure Regulator | 6 | Y | 4 | 00 |  |  | 0001-296-TIN-0058.pdf
Gidgealpa Gas Satellite - Inlet Separation - Gathering Manifold | GIDG INL SEP 115287-GE-0001 | 115287-GE-0001 | Engine-Compressor-GIDG_A050 | Replace Carburettor Diaphragm/s and Gaskets | 3 | Y | 4 | 00 |  |  | 0001-296-TIN-0058.pdf
Gidgealpa Gas Satellite - Inlet Separation - Gathering Manifold | GIDG INL SEP 115287-GE-0001 | 115287-GE-0001 | Engine-Compressor-GIDG_A066 | Replace Fuel Gas GSOV | 6 | Y | 4 | 00 |  |  | 0001-296-TIN-0058.pdf
Gidgealpa Gas Satellite - Inlet Separation - Gathering Manifold | GIDG INL SEP 115287-GE-0001 | 115287-GE-0001 | Engine-Compressor-GIDG_A025 | Replace Engine Crankcase Oil Header Tank In-Line Filter/s | 6 | M | 4 | 00 |  |  | 0001-296-TIN-0058.pdf
Gidgealpa Gas Satellite - Inlet Separation - Gathering Manifold | GIDG INL SEP 115287-GE-0001 | 115287-GE-0001 | Engine-Compressor-GIDG_A026 | Check / Adjust Engine Crankcase Oil Level Controller | 6 | M | 4 | 00 |  |  | 0001-296-TIN-0058.pdf
Gidgealpa Gas Satellite - Inlet Separation - Gathering Manifold | GIDG INL SEP 115287-GE-0001 | 115287-GE-0001 | Engine-Compressor-GIDG_A015 | Change Engine Oil | 6 | W | 4 | 00 |  |  | 0001-296-TIN-0058.pdf
Gidgealpa Gas Satellite - Inlet Separation - Gathering Manifold | GIDG INL SEP 115287-GE-0001 | 115287-GE-0001 | Engine-Compressor-GIDG_A071 | Replace Lube Oil Hoses | 6 | Y | 4 | 00 |  |  | 0001-296-TIN-0058.pdf
Gidgealpa Gas Satellite - Inlet Separation - Gathering Manifold | GIDG INL SEP 115287-GE-0001 | 115287-GE-0001 | Engine-Compressor-GIDG_A016 | Change Engine Oil Filter | 6 | W | 4 | 00 |  |  | 0001-296-TIN-0058.pdf
Gidgealpa Gas Satellite - Inlet Separation - Gathering Manifold | GIDG INL SEP 115287-GE-0001 | 115287-GE-0001 | Engine-Compressor-GIDG_A031 | Check / Replace Lube Oil / Jacket & Auxiliary Water Hoses / Clamps / Seals | 6 | M | 4 | 00 |  |  | 0001-296-TIN-0058.pdf
Gidgealpa Gas Satellite - Inlet Separation - Gathering Manifold | GIDG INL SEP 115287-GE-0001 | 115287-GE-0001 | Engine-Compressor-GIDG_A061 | Inspect / Clean Engine Cooling System Y-strainer | 3 | Y | 4 | 00 |  |  | 0001-296-TIN-0058.pdf
Gidgealpa Gas Satellite - Inlet Separation - Gathering Manifold | GIDG INL SEP 115287-GE-0001 | 115287-GE-0001 | Engine-Compressor-GIDG_A09 | Check / Fill Cooling Systems Fluid Level (Jacket and Auxiliary) | 6 | W | 4 | 00 |  |  | 0001-296-TIN-0058.pdf
Gidgealpa Gas Satellite - Inlet Separation - Gathering Manifold | GIDG INL SEP 115287-GE-0001 | 115287-GE-0001 | Engine-Compressor-GIDG_A041 | Check / Replace Cooling System Bleed Valves and Vents not blocked | 1 | Y | 4 | 00 |  |  | 0001-296-TIN-0058.pdf
Gidgealpa Gas Satellite - Inlet Separation - Gathering Manifold | GIDG INL SEP 115287-GE-0001 | 115287-GE-0001 | Engine-Compressor-GIDG_A040 | Check / Replace Coolant header tank cap/s | 1 | Y | 4 | 00 |  |  | 0001-296-TIN-0058.pdf | 001
Gidgealpa Gas Satellite - Inlet Separation - Gathering Manifold | GIDG INL SEP 115287-GE-0001 | 115287-GE-0001 | Engine-Compressor-GIDG_A053 | Clean / Inspect Aftercooler Core | 3 | Y | 4 | 00 |  |  | 0001-296-TIN-0058.pdf
Gidgealpa Gas Satellite - Inlet Separation - Gathering Manifold | GIDG INL SEP 115287-GE-0001 | 115287-GE-0001 | Engine-Compressor-GIDG_A059 | Replace Main and Aux Water Pumps | 3 | Y | 4 | 00 |  |  | 0001-296-TIN-0058.pdf | 001
Gidgealpa Gas Satellite - Inlet Separation - Gathering Manifold | GIDG INL SEP 115287-GE-0001 | 115287-GE-0001 | Engine-Compressor-GIDG_A057 | Replace Engine Jacket Water Cooling System Thermostats | 3 | Y | 4 | 00 |  |  | 0001-296-TIN-0058.pdf
Gidgealpa Gas Satellite - Inlet Separation - Gathering Manifold | GIDG INL SEP 115287-GE-0001 | 115287-GE-0001 | Engine-Compressor-GIDG_A032 | Inspect / Clean Cooler Package Tubes / Cores External | 6 | M | 4 | 00 |  |  | 0001-296-TIN-0058.pdf | 001
Gidgealpa Gas Satellite - Inlet Separation - Gathering Manifold | GIDG INL SEP 115287-GE-0001 | 115287-GE-0001 | Engine-Compressor-GIDG_A052 | Drain / Clean / Flush / Replace Cooling System (Jacket and Auxiliary) | 3 | Y | 4 | 00 |  |  | 0001-296-TIN-0058.pdf
Gidgealpa Gas Satellite - Inlet Separation - Gathering Manifold | GIDG INL SEP 115287-GE-0001 | 115287-GE-0001 | Engine-Compressor-GIDG_A017 | Test / Adjust Cooling Water Additive Concentration | 6 | W | 4 | 00 |  |  | 0001-296-TIN-0058.pdf | 001
Gidgealpa Gas Satellite - Inlet Separation - Gathering Manifold | GIDG INL SEP 115287-GE-0001 | 115287-GE-0001 | Engine-Compressor-GIDG_A01 | Check Main and Auxiliary Water Pump | 6 | W | 4 | 00 |  |  | 0001-296-TIN-0058.pdf | 001
Gidgealpa Gas Satellite - Inlet Separation - Gathering Manifold | GIDG INL SEP 115287-GE-0001 | 115287-GE-0001 | Engine-Compressor-GIDG_A038 | Check Cooler Drive Coupling / Pulleys | 1 | Y | 4 | 00 |  |  | 0001-296-TIN-0058.pdf
Gidgealpa Gas Satellite - Inlet Separation - Gathering Manifold | GIDG INL SEP 115287-GE-0001 | 115287-GE-0001 | Engine-Compressor-GIDG_A060 | Replace Engine Oil Cooler | 3 | Y | 4 | 00 |  |  | 0001-296-TIN-0058.pdf
Gidgealpa Gas Satellite - Inlet Separation - Gathering Manifold | GIDG INL SEP 115287-GE-0001 | 115287-GE-0001 | Engine-Compressor-GIDG_A036 | Measure / Record Engine Valve Stem Projection | 1 | Y | 4 | 00 |  |  | 0001-296-TIN-0058.pdf | 001
Gidgealpa Gas Satellite - Inlet Separation - Gathering Manifold | GIDG INL SEP 115287-GE-0001 | 115287-GE-0001 | Engine-Compressor-GIDG_A05 | Check / Record Engine Run Hours | 6 | W | 4 | 00 |  |  | 0001-296-TIN-0058.pdf | 001
Gidgealpa Gas Satellite - Inlet Separation - Gathering Manifold | GIDG INL SEP 115287-GE-0001 | 115287-GE-0001 | Engine-Compressor-GIDG_A04 | Check / Correct Engine ECM, Active or Logged Fault Codes | 6 | W | 4 | 00 |  |  | 0001-296-TIN-0058.pdf
Gidgealpa Gas Satellite - Inlet Separation - Gathering Manifold | GIDG INL SEP 115287-GE-0001 | 115287-GE-0001 | Engine-Compressor-GIDG_A03 | Check / Record Crankcase Blowby | 6 | W | 4 | 00 |  |  | 0001-296-TIN-0058.pdf
Gidgealpa Gas Satellite - Inlet Separation - Gathering Manifold | GIDG INL SEP 115287-GE-0001 | 115287-GE-0001 | Engine-Compressor-GIDG_A076 | Replace Exhaust System, Bellows Flex Connection | 6 | Y | 4 | 00 |  |  | 0001-296-TIN-0058.pdf
Gidgealpa Gas Satellite - Inlet Separation - Gathering Manifold | GIDG INL SEP 115287-GE-0001 | 115287-GE-0001 | Engine-Compressor-GIDG_A044 | Replace Exhaust System, Oxygen Sensors | 1 | Y | 4 | 00 |  |  | 0001-296-TIN-0058.pdf
Gidgealpa Gas Satellite - Inlet Separation - Gathering Manifold | GIDG INL SEP 115287-GE-0001 | 115287-GE-0001 | Engine-Compressor-GIDG_A075 | Check / Replace Exhaust System, Lagging / Heat Shields | 6 | Y | 4 | 00 |  |  | 0001-296-TIN-0058.pdf | 001
Gidgealpa Gas Satellite - Inlet Separation - Gathering Manifold | GIDG INL SEP 115287-GE-0001 | 115287-GE-0001 | Engine-Compressor-GIDG_A033 | Check Exhaust System, bellows, muffler, Lagging, etc | 6 | M | 4 | 00 |  |  | 0001-296-TIN-0058.pdf
Gidgealpa Gas Satellite - Inlet Separation - Gathering Manifold | GIDG INL SEP 115287-GE-0001 | 115287-GE-0001 | Engine-Compressor-GIDG_A039 | Inspect Ignition Coils | 1 | Y | 4 | 00 |  |  | 0001-296-TIN-0058.pdf
Gidgealpa Gas Satellite - Inlet Separation - Gathering Manifold | GIDG INL SEP 115287-GE-0001 | 115287-GE-0001 | Engine-Compressor-GIDG_A013 | Check / Adjust Ignition Timing | 6 | W | 4 | 00 |  |  | 0001-296-TIN-0058.pdf
Gidgealpa Gas Satellite - Inlet Separation - Gathering Manifold | GIDG INL SEP 115287-GE-0001 | 115287-GE-0001 | Engine-Compressor-GIDG_A072 | Replace Ignition Cables: Primary and Secondary Connections, harness plugs | 6 | Y | 4 | 00 |  |  | 0001-296-TIN-0058.pdf
Gidgealpa Gas Satellite - Inlet Separation - Gathering Manifold | GIDG INL SEP 115287-GE-0001 | 115287-GE-0001 | Engine-Compressor-GIDG_A029 | Check / Adjust Ignition System Wiring Harnesses | 6 | M | 4 | 00 |  |  | 0001-296-TIN-0058.pdf
Gidgealpa Gas Satellite - Inlet Separation - Gathering Manifold | GIDG INL SEP 115287-GE-0001 | 115287-GE-0001 | Engine-Compressor-GIDG_A023 | Replace / Report Spark Plugs | 6 | M | 4 | 00 |  |  | 0001-296-TIN-0058.pdf
Gidgealpa Gas Satellite - Inlet Separation - Gathering Manifold | GIDG INL SEP 115287-GE-0001 | 115287-GE-0001 | Engine-Compressor-GIDG_A073 | Replace Fan, Jack shaft and Belt Tensioner Bearings | 6 | Y | 4 | 00 |  |  | 0001-296-TIN-0058.pdf
Gidgealpa Gas Satellite - Inlet Separation - Gathering Manifold | GIDG INL SEP 115287-GE-0001 | 115287-GE-0001 | Engine-Compressor-GIDG_A067 | Replace ESM System Wiring Harnesses and ECU | 6 | Y | 4 | 00 |  |  | 0001-296-TIN-0058.pdf
Gidgealpa Gas Satellite - Inlet Separation - Gathering Manifold | GIDG INL SEP 115287-GE-0001 | 115287-GE-0001 | Engine-Compressor-GIDG_A048 | Check Fan hub taper lock | 1 | Y | 4 | 00 |  |  | 0001-296-TIN-0058.pdf
Gidgealpa Gas Satellite - Inlet Separation - Gathering Manifold | GIDG INL SEP 115287-GE-0001 | 115287-GE-0001 | Engine-Compressor-GIDG_A049 | Replace / Adjust Belts - Alternator / Fan Drive / Power Band belt/s | 1 | Y | 4 | 00 |  |  | 0001-296-TIN-0058.pdf | 001
Gidgealpa Gas Satellite - Inlet Separation - Gathering Manifold | GIDG INL SEP 115287-GE-0001 | 115287-GE-0001 | Engine-Compressor-GIDG_A021 | Check Rotating Components - Guards / Screens | 6 | M | 4 | 00 |  |  | 0001-296-TIN-0058.pdf | 001
Gidgealpa Gas Satellite - Inlet Separation - Gathering Manifold | GIDG INL SEP 115287-GE-0001 | 115287-GE-0001 | Engine-Compressor-GIDG_A06 | Check General Walk Around Inspection, (Leaks or Unusual Noises) | 6 | W | 4 | 00 |  |  | 0001-296-TIN-0058.pdf
Gidgealpa Gas Satellite - Inlet Separation - Gathering Manifold | GIDG INL SEP 115287-GE-0001 | 115287-GE-0001 | Engine-Compressor-GIDG_A034 | Check / Tension Engine Mounting Fasteners | 1 | Y | 4 | 00 |  |  | 0001-296-TIN-0058.pdf
Gidgealpa Gas Satellite - Inlet Separation - Gathering Manifold | GIDG INL SEP 115287-GE-0001 | 115287-GE-0001 | Engine-Compressor-GIDG_A018 | Lubricate Fan and Jack shaft or Tensioner bearings | 6 | W | 4 | 00 |  |  | 0001-296-TIN-0058.pdf
Gidgealpa Gas Satellite - Inlet Separation - Gathering Manifold | GIDG INL SEP 115287-GE-0001 | 115287-GE-0001 | Engine-Compressor-GIDG_A068 | Replace All Seals and Gaskets | 6 | Y | 4 | 00 |  |  | 0001-296-TIN-0058.pdf
Gidgealpa Gas Satellite - Inlet Separation - Gathering Manifold | GIDG INL SEP 115287-GE-0001 | 115287-GE-0001 | Engine-Compressor-GIDG_A030 | Wash / Clean Engine (Pressure Clean) | 6 | M | 4 | 00 |  |  | 0001-296-TIN-0058.pdf
Gidgealpa Gas Satellite - Inlet Separation - Gathering Manifold | GIDG INL SEP 115287-GE-0001 | 115287-GE-0001 | Engine-Compressor-GIDG_A045 | Check / Adjust Fan blade pitch | 1 | Y | 4 | 00 |  |  | 0001-296-TIN-0058.pdf
Gidgealpa Gas Satellite - Inlet Separation - Gathering Manifold | GIDG INL SEP 115287-GE-0001 | 115287-GE-0001 | Engine-Compressor-GIDG_A047 | Check Fan hub blade retainers | 1 | Y | 4 | 00 |  |  | 0001-296-TIN-0058.pdf
Gidgealpa Gas Satellite - Inlet Separation - Gathering Manifold | GIDG INL SEP 115287-GE-0001 | 115287-GE-0001 | Engine-Compressor-GIDG_A046 | Check Fan Blade Deflection / Condition | 1 | Y | 4 | 00 |  |  | 0001-296-TIN-0058.pdf
Gidgealpa Gas Satellite - Inlet Separation - Gathering Manifold | GIDG INL SEP 115287-GE-0001 | 115287-GE-0001 | Engine-Compressor-GIDG_A063 | Replace Engine | 6 | Y | 4 | 00 |  |  | 0001-296-TIN-0058.pdf
Gidgealpa Gas Satellite - Inlet Separation - Gathering Manifold | GIDG INL SEP 115287-GE-0001 | 115287-GE-0001 | Engine-Compressor-GIDG_A062 | Check / Adjust Engine Alignment to Driven Equip. | 6 | Y | 4 | 00 |  |  | 0001-296-TIN-0058.pdf
Gidgealpa Gas Satellite - Inlet Separation - Gathering Manifold | GIDG INL SEP 115287-GE-0001 | 115287-GE-0001 | Engine-Compressor-GIDG_A022 | Clean Engine Crankcase Breather | 6 | M | 4 | 00 |  |  | 0001-296-TIN-0058.pdf
Gidgealpa Gas Satellite - Inlet Separation - Gathering Manifold | GIDG INL SEP 115287-GE-0001 | 115287-GE-0001 | Engine-Compressor-GIDG_A010 | Check / Adjust Primary (main) Gas 'A' Regulator(s) | 6 | W | 4 | 00 |  |  | 0001-296-TIN-0058.pdf
Gidgealpa Gas Satellite - Inlet Separation - Gathering Manifold | GIDG INL SEP 115287-GE-0001 | 115287-GE-0001 | Engine-Compressor-GIDG_A07 | Adjust Engine Valve Clearance | 6 | W | 4 | 00 |  |  | 0001-296-TIN-0058.pdf
Gidgealpa Gas Satellite - Inlet Separation - Gathering Manifold | GIDG INL SEP 115287-GE-0001 | 115287-GE-0001 | Engine-Compressor-GIDG_A08 | Check Engine Valve Rotators | 6 | W | 4 | 00 |  |  | 0001-296-TIN-0058.pdf
Gidgealpa Gas Satellite - Inlet Separation - Gathering Manifold | GIDG INL SEP 115287-GE-0001 | 115287-GE-0001 | Engine-Compressor-GIDG_A037 | Check / Record Engine Vibration Damper | 1 | Y | 4 | 00 |  |  | 0001-296-TIN-0058.pdf
Gidgealpa Gas Satellite - Inlet Separation - Gathering Manifold | GIDG INL SEP 115287-GE-0001 | 115287-GE-0001 | Engine-Compressor-GIDG_A028 | Check / Clean / Adjust Magnetic Pickups (Crankshaft, Camshaft, etc) | 6 | M | 4 | 00 |  |  | 0001-296-TIN-0058.pdf
Gidgealpa Gas Satellite - Inlet Separation - Gathering Manifold | GIDG INL SEP 115287-GE-0001 | 115287-GE-0001 | Engine-Compressor-GIDG_A019 | Check / Adjust Belts - Alternator / Fan Drive / Power Band belt | 6 | W | 4 | 00 |  |  | 0001-296-TIN-0058.pdf
Gidgealpa Gas Satellite - Inlet Separation - Gathering Manifold | GIDG INL SEP 115287-GE-0001 | 115287-GE-0001 | Engine-Compressor-GIDG_A069 | Replace All Gas Connection Flex/Braided Hose/s | 6 | Y | 4 | 00 |  |  | 0001-296-TIN-0058.pdf
Gidgealpa Gas Satellite - Inlet Separation - Gathering Manifold | GIDG INL SEP 115287-GE-0001 | 115287-GE-0001 | Engine-Compressor-GIDG_A064 | Replace Jacket & Auxiliary Water Hoses and Seals | 6 | Y | 4 | 00 |  |  | 0001-296-TIN-0058.pdf
Gidgealpa Gas Satellite - Inlet Separation - Gathering Manifold | GIDG INL SEP 115287-GE-0001 | 115287-GE-0001 | Engine-Compressor-GIDG_A058 | Replace Wastegate | 3 | Y | 4 | 00 |  |  | 0001-296-TIN-0058.pdf
Gidgealpa Gas Satellite - Inlet Separation - Gathering Manifold | GIDG INL SEP 115287-GE-0001 | 115287-GE-0001 | Engine-Compressor-GIDG_A055 | Replace Turbo Charger | 3 | Y | 4 | 00 |  |  | 0001-296-TIN-0058.pdf
Gidgealpa Gas Satellite - Inlet Separation - Pig Receiver from Mawson/Kurunda | GIDG INL SEP 1010-PG-004 | 1010-PG-004 | Pig Launcher-GIDG_A05 | Initial chack for Valve Leakage | 12 | M | 07 | 00 |  |  | 2232881.docx
Gidgealpa Gas Satellite - Inlet Separation - Pig Receiver from Mawson/Kurunda | GIDG INL SEP 1010-PG-004 | 1010-PG-004 | Pig Launcher-GIDG_A03 | Inspect the condition & serviceability of the barrel pressure gauge(s), check for leaks, physical damage & corrosion | 12 | M | 07 | 00 |  |  | 2232881.docx
Gidgealpa Gas Satellite - Inlet Separation - Pig Receiver from Mawson/Kurunda | GIDG INL SEP 1010-PG-004 | 1010-PG-004 | Pig Launcher-GIDG_A09 | Check the condition and serviceability of the actuator | 12 | M | 07 | 00 |  |  | 2232881.docx
Gidgealpa Gas Satellite - Inlet Separation - Pig Receiver from Mawson/Kurunda | GIDG INL SEP 1010-PG-004 | 1010-PG-004 | Pig Launcher-GIDG_A06 | Valve Leak Rate Monitoring | 12 | M | 07 | 00 |  |  | 2232881.docx
Gidgealpa Gas Satellite - Inlet Separation - Pig Receiver from Mawson/Kurunda | GIDG INL SEP 1010-PG-004 | 1010-PG-004 | Pig Launcher-GIDG_A010 | Check the condition and serviceability of all drain/vent ports | 12 | M | 07 | 00 |  |  | 2232881.docx
Gidgealpa Gas Satellite - Inlet Separation - Pig Receiver from Mawson/Kurunda | GIDG INL SEP 1010-PG-004 | 1010-PG-004 | Pig Launcher-GIDG_A04 | Check the condition and serviceability of the Pig Signal(s); verify that all fixings and linkages are secure | 12 | M | 07 | 00 |  |  | 2232881.docx
Gidgealpa Gas Satellite - Inlet Separation - Pig Receiver from Mawson/Kurunda | GIDG INL SEP 1010-PG-004 | 1010-PG-004 | Pig Launcher-GIDG_A02 | Function Check Pressure Gauge | 12 | M | 07 | 00 |  |  | 2232881.docx
Gidgealpa Gas Satellite - Inlet Separation - Pig Receiver from Mawson/Kurunda | GIDG INL SEP 1010-PG-004 | 1010-PG-004 | Pig Launcher-GIDG_A08 | Check the condition and serviceability of the gearbox | 12 | M | 07 | 00 |  |  | 2232881.docx
Gidgealpa Gas Satellite - Inlet Separation - Pig Receiver from Mawson/Kurunda | GIDG INL SEP 1010-PG-004 | 1010-PG-004 | Pig Launcher-GIDG_A011 | Check Exercise valves that there are no abnormal noises or vibration | 12 | M | 07 | 00 |  |  | 2232881.docx
Gidgealpa Gas Satellite - Inlet Separation - Pig Receiver from Mawson/Kurunda | GIDG INL SEP 1010-PG-004 | 1010-PG-004 | Pig Launcher-GIDG_A01 | Inspect the condition & serviceability of all piping valves and actuator/gearbox assemblies | 12 | M | 07 | 00 |  |  | 2232881.docx
Gidgealpa Gas Satellite - Inlet Separation - Pig Receiver from Mawson/Kurunda | GIDG INL SEP 1010-PG-004 | 1010-PG-004 | Pig Launcher-GIDG_A012 | Final check for Valve Leakage | 12 | M | 07 | 00 |  |  | 2232881.docx
Gidgealpa Gas Satellite - Inlet Separation - Pig Receiver from Mawson/Kurunda | GIDG INL SEP 1010-PG-004 | 1010-PG-004 | Pig Launcher-GIDG_A07 | Grease Valve Stem | 12 | M | 07 | 00 |  |  | 2232881.docx
Gidgealpa Gas Satellite - Inlet Separation - Pig Receiver Jack Lake to Gidgealpa | GIDG INL SEP 1018-PG-002 | 1018-PG-002 | Pig Launcher-GIDG_A07 | Grease Valve Stem | 12 | M | 07 | 00 |  |  | 2232881.docx
Gidgealpa Gas Satellite - Inlet Separation - Pig Receiver Jack Lake to Gidgealpa | GIDG INL SEP 1018-PG-002 | 1018-PG-002 | Pig Launcher-GIDG_A010 | Check the condition and serviceability of all drain/vent ports | 12 | M | 07 | 00 |  |  | 2232881.docx
Gidgealpa Gas Satellite - Inlet Separation - Pig Receiver Jack Lake to Gidgealpa | GIDG INL SEP 1018-PG-002 | 1018-PG-002 | Pig Launcher-GIDG_A04 | Check the condition and serviceability of the Pig Signal(s); verify that all fixings and linkages are secure | 12 | M | 07 | 00 |  |  | 2232881.docx
Gidgealpa Gas Satellite - Inlet Separation - Pig Receiver Jack Lake to Gidgealpa | GIDG INL SEP 1018-PG-002 | 1018-PG-002 | Pig Launcher-GIDG_A03 | Inspect the condition & serviceability of the barrel pressure gauge(s), check for leaks, physical damage & corrosion | 12 | M | 07 | 00 |  |  | 2232881.docx
Gidgealpa Gas Satellite - Inlet Separation - Pig Receiver Jack Lake to Gidgealpa | GIDG INL SEP 1018-PG-002 | 1018-PG-002 | Pig Launcher-GIDG_A02 | Function Check Pressure Gauge | 12 | M | 07 | 00 |  |  | 2232881.docx
Gidgealpa Gas Satellite - Inlet Separation - Pig Receiver Jack Lake to Gidgealpa | GIDG INL SEP 1018-PG-002 | 1018-PG-002 | Pig Launcher-GIDG_A08 | Check the condition and serviceability of the gearbox | 12 | M | 07 | 00 |  |  | 2232881.docx
Gidgealpa Gas Satellite - Inlet Separation - Pig Receiver Jack Lake to Gidgealpa | GIDG INL SEP 1018-PG-002 | 1018-PG-002 | Pig Launcher-GIDG_A011 | Check Exercise valves that there are no abnormal noises or vibration | 12 | M | 07 | 00 |  |  | 2232881.docx
Gidgealpa Gas Satellite - Inlet Separation - Pig Receiver Jack Lake to Gidgealpa | GIDG INL SEP 1018-PG-002 | 1018-PG-002 | Pig Launcher-GIDG_A01 | Inspect the condition & serviceability of all piping valves and actuator/gearbox assemblies | 12 | M | 07 | 00 |  |  | 2232881.docx
Gidgealpa Gas Satellite - Inlet Separation - Pig Receiver Jack Lake to Gidgealpa | GIDG INL SEP 1018-PG-002 | 1018-PG-002 | Pig Launcher-GIDG_A012 | Final check for Valve Leakage | 12 | M | 07 | 00 |  |  | 2232881.docx
Gidgealpa Gas Satellite - Inlet Separation - Pig Receiver Jack Lake to Gidgealpa | GIDG INL SEP 1018-PG-002 | 1018-PG-002 | Pig Launcher-GIDG_A05 | Initial chack for Valve Leakage | 12 | M | 07 | 00 |  |  | 2232881.docx
Gidgealpa Gas Satellite - Inlet Separation - Pig Receiver Jack Lake to Gidgealpa | GIDG INL SEP 1018-PG-002 | 1018-PG-002 | Pig Launcher-GIDG_A09 | Check the condition and serviceability of the actuator | 12 | M | 07 | 00 |  |  | 2232881.docx
Gidgealpa Gas Satellite - Inlet Separation - Pig Receiver Jack Lake to Gidgealpa | GIDG INL SEP 1018-PG-002 | 1018-PG-002 | Pig Launcher-GIDG_A06 | Valve Leak Rate Monitoring | 12 | M | 07 | 00 |  |  | 2232881.docx | 001
Gidgealpa Gas Satellite - Instrument Air Supply - Air Desiccant Dryer Package | GIDG INST AIR 1010-DX-001 | 1010-DX-001 | Instrument Air KEN-GIDG_A01 | Check dryer is operational. Report faults as required | 1 | W | 44 | 01 | 1010-DX-001 1W-44-01-001 | 1010-DX-001 1W-44-01-001 | OEC Tasks List | 001
Gidgealpa Gas Satellite - Instrument Air Supply - Air Desiccant Dryer Package | GIDG INST AIR 1010-DX-001 | 1010-DX-001 | Instrument Air KEN-GIDG_A02 | Carry out Inspection & Replacement Task Absorption Dryer Skid for Control Panel & Dew-point Sensor | 1 | Y | 01 | 00 |  |  | 0010-295-TIN-0004.pdf
Gidgealpa Gas Satellite - Instrument Air Supply - Air Desiccant Dryer Package | GIDG INST AIR 1010-DX-001 | 1010-DX-001 | Instrument Air KEN-GIDG_A04 | Carry out Inspection of dust sieve | 1 | Y | 4 | 00 |  |  | 0010-296-TIN-0064.pdf
Gidgealpa Gas Satellite - Instrument Air Supply - Air Desiccant Dryer Package | GIDG INST AIR 1010-DX-001 | 1010-DX-001 | Instrument Air KEN-GIDG_A05 | Carry out Replacement of drying agent | 1 | Y | 4 | 00 |  |  | 0010-296-TIN-0064.pdf
Gidgealpa Gas Satellite - Instrument Air Supply - Air Desiccant Dryer Package | GIDG INST AIR 1010-DX-001 | 1010-DX-001 | Instrument Air KEN-GIDG_A03 | Carry out Replacement of muffler & inlet/outlet filter | 1 | Y | 4 | 00 |  |  | 0010-296-TIN-0064.pdf
Gidgealpa Gas Satellite - Instrument Air Supply - Air Desiccant Dryer Package | GIDG INST AIR 1010-DX-001 | 1010-DX-001 | Instrument Air KEN-GIDG_A07 | Carry out Inspection & Replacement Task for Absorption Dryer Skid, Directional Block Valve, Vessel B Inlet | 2 | Y | 01 | 00 |  |  | 0010-295-TIN-0005.pdf
Gidgealpa Gas Satellite - Instrument Air Supply - Air Desiccant Dryer Package | GIDG INST AIR 1010-DX-001 | 1010-DX-001 | Instrument Air KEN-GIDG_A08 | Carry out Inspection & Function Check for Absorption Dryer Skid, Check Valves | 2 | Y | 01 | 00 |  |  | 0010-295-TIN-0005.pdf
Gidgealpa Gas Satellite - Instrument Air Supply - Air Desiccant Dryer Package | GIDG INST AIR 1010-DX-001 | 1010-DX-001 | Instrument Air KEN-GIDG_A010 | Carry out Inspection & Function Check for Dryer Skid, Discharge Pressure Switch / By-pass Control Loop | 4 | Y | 01 | 00 |  |  | 0010-295-TIN-0006.pdf
Gidgealpa Gas Satellite - Instrument Air Supply - Air Desiccant Dryer Package | GIDG INST AIR 1010-DX-001 | 1010-DX-001 | Instrument Air KEN-GIDG_A06 | Carry out Inspection & Function Check for Absorption Dryer Skid, Directional Block Valve, Vessel A Inlet | 2 | Y | 01 | 00 |  |  | 0010-295-TIN-0005.pdf
Gidgealpa Gas Satellite - Instrument Air Supply - Air Desiccant Dryer Package | GIDG INST AIR 1010-DX-001 | 1010-DX-001 | Instrument Air KEN-GIDG_A011 | Carry out Inspection & Replacement Task for Absorption Dryer Skid, Directional Block Valve, Vessel A Inlet | 4 | Y | 01 | 00 |  |  | 0010-295-TIN-0006.pdf
Gidgealpa Gas Satellite - Instrument Air Supply - Air Desiccant Dryer Package | GIDG INST AIR 1010-DX-001 | 1010-DX-001 | Instrument Air KEN-GIDG_A09 | Carry out Inspection & Replacement Task for Absorption Dryer Skid, Control Panel & Dew-point Sensor | 2 | Y | 01 | 00 |  |  | 0010-295-TIN-0005.pdf
Gidgealpa Gas Satellite - Instrument Air Supply - Instrument Air Package A | GIDG INST AIR 1010-K-004A | 1010-K-004A | Compressor-Air Champion CSF22-GIDG_A042 | Replace purge filter element | 1 | Y | 4 | 00 |  |  | 0010-296-TIN-0092.pdf
Gidgealpa Gas Satellite - Instrument Air Supply - Instrument Air Package A | GIDG INST AIR 1010-KX-004A | 1010-KX-004A | Compressor Package IE-Air Champion CSF22-GIDG_A07 | Inspect solenoid for damage and unauthorized modifications | 1 | Y | 01 | 00 |  |  | 0010-295-TIN-0003.pdf
Gidgealpa Gas Satellite - Instrument Air Supply - Instrument Air Package A | GIDG INST AIR 1010-KX-004A | 1010-KX-004A | Compressor Package IE-Air Champion CSF22-GIDG_A01 | Inspect switches for damage and unauthorized modifications | 1 | Y | 01 | 00 |  |  | 0010-295-TIN-0003.pdf
Gidgealpa Gas Satellite - Instrument Air Supply - Instrument Air Package A | GIDG INST AIR 1010-KX-004A | 1010-KX-004A | Compressor Package IE-Air Champion CSF22-GIDG_A11 | Inspect all motor air cooling paths to ensure they are clear. Clean as required | 1 | Y | 01 | 00 |  |  | 0010-295-TIN-0003.pdf | 001
Gidgealpa Gas Satellite - Instrument Air Supply - Instrument Air Package A | GIDG INST AIR 1010-KX-004A | 1010-KX-004A | Compressor Package IE-Air Champion CSF22-GIDG_A10 | Check condition of control tubing and small bore fittings | 1 | Y | 01 | 00 |  |  | 0010-295-TIN-0003.pdf
Gidgealpa Gas Satellite - Instrument Air Supply - Instrument Air Package A | GIDG INST AIR 1010-KX-004A | 1010-KX-004A | Compressor Package IE-Air Champion CSF22-GIDG_A05 | Inspect condition of internal wiring and connections for damage and security | 1 | Y | 01 | 00 |  |  | 0010-295-TIN-0003.pdf
Gidgealpa Gas Satellite - Instrument Air Supply - Instrument Air Package A | GIDG INST AIR 1010-KX-004A | 1010-KX-004A | Compressor Package IE-Air Champion CSF22-GIDG_A03 | Inspect condition of all cabling. Ensure all connections are tight | 1 | Y | 01 | 00 |  |  | 0010-295-TIN-0003.pdf
Gidgealpa Gas Satellite - Instrument Air Supply - Instrument Air Package A | GIDG INST AIR 1010-KX-004A | 1010-KX-004A | Compressor Package IE-Air Champion CSF22-GIDG_A15 | Ensure that the high temperature shutdown indicator on the control panel is lit | 4 | Y | 01 | 00 |  |  | 0010-295-TIN-0002.pdf
Gidgealpa Gas Satellite - Instrument Air Supply - Instrument Air Package A | GIDG INST AIR 1010-KX-004A | 1010-KX-004A | Compressor Package IE-Air Champion CSF22-GIDG_A14 | Inspect temperature sensor cabling and all connections | 4 | Y | 01 | 00 |  |  | 0010-295-TIN-0002.pdf
Gidgealpa Gas Satellite - Instrument Air Supply - Instrument Air Package A | GIDG INST AIR 1010-KX-004A | 1010-KX-004A | Compressor Package IE-Air Champion CSF22-GIDG_A13 | Check operation of differential pressure switches | 4 | Y | 01 | 00 |  |  | 0010-295-TIN-0002.pdf
Gidgealpa Gas Satellite - Instrument Air Supply - Instrument Air Package A | GIDG INST AIR 1010-KX-004A | 1010-KX-004A | Compressor Package IE-Air Champion CSF22-GIDG_A04 | Inspect the compressor control panel for damage | 1 | Y | 01 | 00 |  |  | 0010-295-TIN-0003.pdf
Gidgealpa Gas Satellite - Instrument Air Supply - Instrument Air Package A | GIDG INST AIR 1010-KX-004A | 1010-KX-004A | Compressor Package IE-Air Champion CSF22-GIDG_A02 | Inspect condition of all tube work, checking for leaks | 1 | Y | 01 | 00 |  |  | 0010-295-TIN-0003.pdf
Gidgealpa Gas Satellite - Instrument Air Supply - Instrument Air Package A | GIDG INST AIR 1010-KX-004A | 1010-KX-004A | Compressor Package IE-Air Champion CSF22-GIDG_A12 | Inspect motor frame for signs of cracking especially in the motor mounting areas | 1 | Y | 01 | 00 |  |  | 0010-295-TIN-0003.pdf
Gidgealpa Gas Satellite - Instrument Air Supply - Instrument Air Package A | GIDG INST AIR 1010-KX-004A | 1010-KX-004A | Compressor Package IE-Air Champion CSF22-GIDG_A06 | Clean plug connections using contact cleaner | 1 | Y | 01 | 00 |  |  | 0010-295-TIN-0003.pdf
Gidgealpa Gas Satellite - Instrument Air Supply - Instrument Air Package A | GIDG INST AIR 1010-KX-004A | 1010-KX-004A | Compressor Package IE-Air Champion CSF22-GIDG_A08 | Check condition and serviceability of the Motor | 1 | Y | 01 | 00 |  |  | 0010-295-TIN-0003.pdf
Gidgealpa Gas Satellite - Instrument Air Supply - Instrument Air Package A | GIDG INST AIR 1010-K-004A | 1010-K-004A | Compressor-Air Champion CSF22-GIDG_A035 | Lubricate electric motor bearings | 3 | M | 4 | 00 |  |  | 0010-296-TIN-0090.pdf
Gidgealpa Gas Satellite - Instrument Air Supply - Instrument Air Package A | GIDG INST AIR 1010-K-004A | 1010-K-004A | Compressor-Air Champion CSF22-GIDG_A027 | Inspect pulley profile for excessive wear, Replace motor and airend pulleys as required. | 3 | M | 4 | 00 |  |  | 0010-296-TIN-0090.pdf
Gidgealpa Gas Satellite - Instrument Air Supply - Instrument Air Package A | GIDG INST AIR 1010-KX-004A | 1010-KX-004A | Compressor Package IE-Air Champion CSF22-GIDG_A09 | Inspect Motor for damage and unauthorized modifications | 1 | Y | 01 | 00 |  |  | 0010-295-TIN-0003.pdf
Gidgealpa Gas Satellite - Instrument Air Supply - Instrument Air Package A | GIDG INST AIR 1010-K-004A | 1010-K-004A | Compressor-Air Champion CSF22-GIDG_A051 | Replace seal, check spring, piston spring, o-ring and screws using repair kit | 1 | Y | 4 | 00 |  |  | 0010-296-TIN-0092.pdf
Gidgealpa Gas Satellite - Instrument Air Supply - Instrument Air Package A | GIDG INST AIR 1010-K-004A | 1010-K-004A | Compressor-Air Champion CSF22-GIDG_A044 | Replace valve plate, piston, cup seal and 3 x o-rings using seal repair kit | 1 | Y | 4 | 00 |  |  | 0010-296-TIN-0092.pdf
Gidgealpa Gas Satellite - Instrument Air Supply - Instrument Air Package A | GIDG INST AIR 1010-K-004A | 1010-K-004A | Compressor-Air Champion CSF22-GIDG_A053 | Replace thermostat, slide, and seal using repair kit | 1 | Y | 4 | 00 |  |  | 0010-296-TIN-0092.pdf
Gidgealpa Gas Satellite - Instrument Air Supply - Instrument Air Package A | GIDG INST AIR 1010-K-004A | 1010-K-004A | Compressor-Air Champion CSF22-GIDG_A064 | Inspect all motor air cooling paths to ensure they are clear | 1 | Y | 4 | 00 |  |  | 0010-296-TIN-0092.pdf
Gidgealpa Gas Satellite - Instrument Air Supply - Instrument Air Package A | GIDG INST AIR 1010-K-004A | 1010-K-004A | Compressor-Air Champion CSF22-GIDG_A022 | Replace flexible hosing and clamps | 3 | M | 4 | 00 |  |  | 0010-296-TIN-0090.pdf
Gidgealpa Gas Satellite - Instrument Air Supply - Instrument Air Package A | GIDG INST AIR 1010-K-004A | 1010-K-004A | Compressor-Air Champion CSF22-GIDG_A058 | Replace flexible hosing, and clamps | 1 | Y | 4 | 00 |  |  | 0010-296-TIN-0092.pdf
Gidgealpa Gas Satellite - Instrument Air Supply - Instrument Air Package A | GIDG INST AIR 1010-K-004A | 1010-K-004A | Compressor-Air Champion CSF22-GIDG_A066 | Check for leaks in all plumbing, tube work and filter seals | 1 | Y | 4 | 00 |  |  | 0010-296-TIN-0092.pdf
Gidgealpa Gas Satellite - Instrument Air Supply - Instrument Air Package A | GIDG INST AIR 1010-K-004A | 1010-K-004A | Compressor-Air Champion CSF22-GIDG_A050 | Re-connect air intake plumbing | 1 | Y | 4 | 00 |  |  | 0010-296-TIN-0092.pdf
Gidgealpa Gas Satellite - Instrument Air Supply - Instrument Air Package A | GIDG INST AIR 1010-K-004A | 1010-K-004A | Compressor-Air Champion CSF22-GIDG_A03 | Check inside the enclosure for leaks or other faults | 1 | W | 44 | 01 | 1010-K-004A 1W-44-01- | 1010-K-004A 1W-44-01- | OEC Tasks List
Gidgealpa Gas Satellite - Instrument Air Supply - Instrument Air Package A | GIDG INST AIR 1010-K-004A | 1010-K-004A | Compressor-Air Champion CSF22-GIDG_A034 | Check all nuts, bolts and pipe fittings are tight | 3 | M | 4 | 00 |  |  | 0010-296-TIN-0090.pdf
Gidgealpa Gas Satellite - Instrument Air Supply - Instrument Air Package A | GIDG INST AIR 1010-K-004A | 1010-K-004A | Compressor-Air Champion CSF22-GIDG_A01 | Check the local panel to ensure the unit is opeational and ready to start if in standby mode | 1 | W | 44 | 01 | 1010-K-004A 1W-44-01- | 1010-K-004A 1W-44-01- | OEC Tasks List
Gidgealpa Gas Satellite - Instrument Air Supply - Instrument Air Package A | GIDG INST AIR 1010-K-004A | 1010-K-004A | Compressor-Air Champion CSF22-GIDG_A049 | Replace VMC style inlet controller | 1 | Y | 4 | 00 |  |  | 0010-296-TIN-0092.pdf
Gidgealpa Gas Satellite - Instrument Air Supply - Instrument Air Package A | GIDG INST AIR 1010-K-004A | 1010-K-004A | Compressor-Air Champion CSF22-GIDG_A033 | Inspect pre-filter mat fitted to the front cabinet panel | 3 | M | 4 | 00 |  |  | 0010-296-TIN-0090.pdf | 001
Gidgealpa Gas Satellite - Instrument Air Supply - Instrument Air Package A | GIDG INST AIR 1010-K-004A | 1010-K-004A | Compressor-Air Champion CSF22-GIDG_A063 | Replace pre-filter mat fitted to the front cabinet panel with new | 1 | Y | 4 | 00 |  |  | 0010-296-TIN-0092.pdf
Gidgealpa Gas Satellite - Instrument Air Supply - Instrument Air Package A | GIDG INST AIR 1010-K-004A | 1010-K-004A | Compressor-Air Champion CSF22-GIDG_A032 | Clean out compressor cabinet and remove dirt and grime from components | 3 | M | 4 | 00 |  |  | 0010-296-TIN-0090.pdf | 001
Gidgealpa Gas Satellite - Instrument Air Supply - Instrument Air Package A | GIDG INST AIR 1010-K-004A | 1010-K-004A | Compressor-Air Champion CSF22-GIDG_A02 | Check Belts for tension, noise and wear. Raise WO to rectify as needed | 1 | W | 44 | 01 | 1010-K-004A 1W-44-01-001 | 1010-K-004A 1W-44-01-001 | OEC Tasks List | 001
Gidgealpa Gas Satellite - Instrument Air Supply - Instrument Air Package A | GIDG INST AIR 1010-K-004A | 1010-K-004A | Compressor-Air Champion CSF22-GIDG_A037 | Re-tension the separator bolts to 77 Nm (57ft.lbs). | 3 | M | 4 | 00 |  |  | 0010-296-TIN-0090.pdf
Gidgealpa Gas Satellite - Instrument Air Supply - Instrument Air Package A | GIDG INST AIR 1010-K-004A | 1010-K-004A | Compressor-Air Champion CSF22-GIDG_A028 | Inspect taper lock bushes and file off burrs, replace if required. | 3 | M | 4 | 00 |  |  | 0010-296-TIN-0090.pdf
Gidgealpa Gas Satellite - Instrument Air Supply - Instrument Air Package A | GIDG INST AIR 1010-K-004A | 1010-K-004A | Compressor-Air Champion CSF22-GIDG_A043 | Overhaul intake control valve | 1 | Y | 4 | 00 |  |  | 0010-296-TIN-0092.pdf
Gidgealpa Gas Satellite - Instrument Air Supply - Instrument Air Package A | GIDG INST AIR 1010-K-004A | 1010-K-004A | Compressor-Air Champion CSF22-GIDG_A018 | Remove air filter element by gently easing it downwards | 3 | M | 4 | 00 |  |  | 0010-296-TIN-0090.pdf
Gidgealpa Gas Satellite - Instrument Air Supply - Instrument Air Package A | GIDG INST AIR 1010-K-004A | 1010-K-004A | Compressor-Air Champion CSF22-GIDG_A030 | Check parallel alignment of pulleys and belts following pulley replacement and/or belt replacement | 3 | M | 4 | 00 |  |  | 0010-296-TIN-0090.pdf
Gidgealpa Gas Satellite - Instrument Air Supply - Instrument Air Package A | GIDG INST AIR 1010-K-004A | 1010-K-004A | Compressor-Air Champion CSF22-GIDG_A019 | Clean the base and interior of the air filter cover using a damp cloth | 3 | M | 4 | 00 |  |  | 0010-296-TIN-0090.pdf
Gidgealpa Gas Satellite - Instrument Air Supply - Instrument Air Package A | GIDG INST AIR 1010-K-004A | 1010-K-004A | Compressor-Air Champion CSF22-GIDG_A024 | Re-tension belts as required by tightening the tensioning | 3 | M | 4 | 00 |  |  | 0010-296-TIN-0090.pdf
Gidgealpa Gas Satellite - Instrument Air Supply - Instrument Air Package A | GIDG INST AIR 1010-K-004A | 1010-K-004A | Compressor-Air Champion CSF22-GIDG_A052 | Check the condition of the valve plate, housing and stem, remove any burrs and replace if necessary | 1 | Y | 4 | 00 |  |  | 0010-296-TIN-0092.pdf
Gidgealpa Gas Satellite - Instrument Air Supply - Instrument Air Package A | GIDG INST AIR 1010-K-004A | 1010-K-004A | Compressor-Air Champion CSF22-GIDG_A029 | Recheck the belt tension FIVE minutes after a new set of belts are fitted and then again TEN minutes later, re-tension as required | 3 | M | 4 | 00 |  |  | 0010-296-TIN-0090.pdf
Gidgealpa Gas Satellite - Instrument Air Supply - Instrument Air Package A | GIDG INST AIR 1010-K-004A | 1010-K-004A | Compressor-Air Champion CSF22-GIDG_A048 | Replace the gasket between the inlet control valve and the air end | 1 | Y | 4 | 00 |  |  | 0010-296-TIN-0092.pdf
Gidgealpa Gas Satellite - Instrument Air Supply - Instrument Air Package A | GIDG INST AIR 1010-K-004A | 1010-K-004A | Compressor-Air Champion CSF22-GIDG_A023 | Remove the belt guard and inspect the condition and serviceability of the vee belts, replace all belts | 3 | M | 4 | 00 |  |  | 0010-296-TIN-0090.pdf
Gidgealpa Gas Satellite - Instrument Air Supply - Instrument Air Package A | GIDG INST AIR 1010-K-004A | 1010-K-004A | Compressor-Air Champion CSF22-GIDG_A060 | Inspect pulleys for contamination and clean as required | 1 | Y | 4 | 00 |  |  | 0010-296-TIN-0092.pdf | 001
Gidgealpa Gas Satellite - Instrument Air Supply - Instrument Air Package A | GIDG INST AIR 1010-K-004A | 1010-K-004A | Compressor-Air Champion CSF22-GIDG_A054 | Refit to thermo-valve body and replace plug | 1 | Y | 4 | 00 |  |  | 0010-296-TIN-0092.pdf
Gidgealpa Gas Satellite - Instrument Air Supply - Instrument Air Package A | GIDG INST AIR 1010-K-004A | 1010-K-004A | Compressor-Air Champion CSF22-GIDG_A055 | Reassemble MPV assembly | 1 | Y | 4 | 00 |  |  | 0010-296-TIN-0092.pdf | 001
Gidgealpa Gas Satellite - Instrument Air Supply - Instrument Air Package A | GIDG INST AIR 1010-K-004A | 1010-K-004A | Compressor-Air Champion CSF22-GIDG_A040 | Replace with a new separator element and gasket assembly & reassemble filter assembly | 1 | Y | 4 | 00 |  |  | 0010-296-TIN-0092.pdf
Gidgealpa Gas Satellite - Instrument Air Supply - Instrument Air Package A | GIDG INST AIR 1010-K-004A | 1010-K-004A | Compressor-Air Champion CSF22-GIDG_A026 | Remove tension in existing belts | 3 | M | 4 | 00 |  |  | 0010-296-TIN-0090.pdf | 001
Gidgealpa Gas Satellite - Instrument Air Supply - Instrument Air Package A | GIDG INST AIR 1010-K-004A | 1010-K-004A | Compressor-Air Champion CSF22-GIDG_A031 | Check that the rear face of the airend pulley is positioned 10mm off the mounting face | 3 | M | 4 | 00 |  |  | 0010-296-TIN-0090.pdf | 001
Gidgealpa Gas Satellite - Instrument Air Supply - Instrument Air Package A | GIDG INST AIR 1010-K-004A | 1010-K-004A | Compressor-Air Champion CSF22-GIDG_A059 | Remove existing belts | 1 | Y | 4 | 00 |  |  | 0010-296-TIN-0092.pdf
Gidgealpa Gas Satellite - Instrument Air Supply - Instrument Air Package A | GIDG INST AIR 1010-K-004A | 1010-K-004A | Compressor-Air Champion CSF22-GIDG_A025 | Re-fit belt guard | 3 | M | 4 | 00 |  |  | 0010-296-TIN-0090.pdf
Gidgealpa Gas Satellite - Instrument Air Supply - Instrument Air Package A | GIDG INST AIR 1010-K-004A | 1010-K-004A | Compressor-Air Champion CSF22-GIDG_A047 | Re-fit intake controller assembly to air end | 1 | Y | 4 | 00 |  |  | 0010-296-TIN-0092.pdf
Gidgealpa Gas Satellite - Instrument Air Supply - Instrument Air Package A | GIDG INST AIR 1010-K-004A | 1010-K-004A | Compressor-Air Champion CSF22-GIDG_A015 | Hand-tighten the new element until the o-ring is seated and tighten an additional 1/2 to 3/4 of a turn | 3 | M | 4 | 00 |  |  | 0010-296-TIN-0090.pdf
Gidgealpa Gas Satellite - Instrument Air Supply - Instrument Air Package A | GIDG INST AIR 1010-K-004A | 1010-K-004A | Compressor-Air Champion CSF22-GIDG_A021 | Replace the housing cover, ensuring both clips are correctly located and secured | 3 | M | 4 | 00 |  |  | 0010-296-TIN-0090.pdf
Gidgealpa Gas Satellite - Instrument Air Supply - Instrument Air Package A | GIDG INST AIR 1010-K-004A | 1010-K-004A | Compressor-Air Champion CSF22-GIDG_A020 | Inspect the condition and serviceability of the Air Inlet Filter element, replace as required | 3 | M | 4 | 00 |  |  | 0010-296-TIN-0090.pdf | 001
Gidgealpa Gas Satellite - Instrument Air Supply - Instrument Air Package A | GIDG INST AIR 1010-K-004A | 1010-K-004A | Compressor-Air Champion CSF22-GIDG_A038 | Re-fit compressor cabinet panels | 3 | M | 4 | 00 |  |  | 0010-296-TIN-0090.pdf | 001
Gidgealpa Gas Satellite - Instrument Air Supply - Instrument Air Package A | GIDG INST AIR 1010-K-004A | 1010-K-004A | Compressor-Air Champion CSF22-GIDG_A062 | Inspect fan hub is centred within the cowling. adjust & clean as required | 1 | Y | 4 | 00 |  |  | 0010-296-TIN-0092.pdf
Gidgealpa Gas Satellite - Instrument Air Supply - Instrument Air Package A | GIDG INST AIR 1010-K-004A | 1010-K-004A | Compressor-Air Champion CSF22-GIDG_A065 | Clean down compressor package on completion of service, if required | 1 | Y | 4 | 00 |  |  | 0010-296-TIN-0092.pdf
Gidgealpa Gas Satellite - Instrument Air Supply - Instrument Air Package A | GIDG INST AIR 1010-K-004A | 1010-K-004A | Compressor-Air Champion CSF22-GIDG_A016 | Clean the exterior of the air filter cover | 3 | M | 4 | 00 |  |  | 0010-296-TIN-0090.pdf
Gidgealpa Gas Satellite - Instrument Air Supply - Instrument Air Package A | GIDG INST AIR 1010-K-004A | 1010-K-004A | Compressor-Air Champion CSF22-GIDG_A013 | Clean the o-ring seating surface | 3 | M | 4 | 00 |  |  | 0010-296-TIN-0090.pdf
Gidgealpa Gas Satellite - Instrument Air Supply - Instrument Air Package A | GIDG INST AIR 1010-K-004A | 1010-K-004A | Compressor-Air Champion CSF22-GIDG_A017 | Remove air filter cover by pressing the quick release clips | 3 | M | 4 | 00 |  |  | 0010-296-TIN-0090.pdf
Gidgealpa Gas Satellite - Instrument Air Supply - Instrument Air Package A | GIDG INST AIR 1010-K-004A | 1010-K-004A | Compressor-Air Champion CSF22-GIDG_A046 | Inspect the compressor rotors for excessive scoring or damage | 1 | Y | 4 | 00 |  |  | 0010-296-TIN-0092.pdf
Gidgealpa Gas Satellite - Instrument Air Supply - Instrument Air Package A | GIDG INST AIR 1010-K-004A | 1010-K-004A | Compressor-Air Champion CSF22-GIDG_A036 | Check oil level and top up if necessary | 3 | M | 4 | 00 |  |  | 0010-296-TIN-0090.pdf
Gidgealpa Gas Satellite - Instrument Air Supply - Instrument Air Package A | GIDG INST AIR 1010-K-004A | 1010-K-004A | Compressor-Air Champion CSF22-GIDG_A04 | Check lube oil level and top-up if necessary | 1 | W | 44 | 01 | 1010-K-004A 1W-44-01- | 1010-K-004A 1W-44-01- | OEC Tasks List
Gidgealpa Gas Satellite - Instrument Air Supply - Instrument Air Package A | GIDG INST AIR 1010-K-004A | 1010-K-004A | Compressor-Air Champion CSF22-GIDG_A010 | Replace the oil filler cap and ensure that the O-ring is properly seated | 3 | M | 4 | 00 |  |  | 0010-296-TIN-0090.pdf
Gidgealpa Gas Satellite - Instrument Air Supply - Instrument Air Package A | GIDG INST AIR 1010-K-004A | 1010-K-004A | Compressor-Air Champion CSF22-GIDG_A09 | Remove the oil filler cap and refill the Air-Oil Separator (sump) as required | 3 | M | 4 | 00 |  |  | 0010-296-TIN-0090.pdf
Gidgealpa Gas Satellite - Instrument Air Supply - Instrument Air Package A | GIDG INST AIR 1010-K-004A | 1010-K-004A | Compressor-Air Champion CSF22-GIDG_A08 | Ensure oil analysis label is attached to sample bottle and record compressor run hours | 3 | M | 4 | 00 |  |  | 0010-296-TIN-0090.pdf
Gidgealpa Gas Satellite - Instrument Air Supply - Instrument Air Package A | GIDG INST AIR 1010-K-004A | 1010-K-004A | Compressor-Air Champion CSF22-GIDG_A011 | Inspect purge filter, clean if required | 3 | M | 4 | 00 |  |  | 0010-296-TIN-0090.pdf
Gidgealpa Gas Satellite - Instrument Air Supply - Instrument Air Package A | GIDG INST AIR 1010-K-004A | 1010-K-004A | Compressor-Air Champion CSF22-GIDG_A014 | Apply a light film of compressor oil to the new o-ring | 3 | M | 4 | 00 |  |  | 0010-296-TIN-0090.pdf
Gidgealpa Gas Satellite - Instrument Air Supply - Instrument Air Package A | GIDG INST AIR 1010-K-004A | 1010-K-004A | Compressor-Air Champion CSF22-GIDG_A05 | Take an oil sample, after shutting down | 3 | M | 4 | 00 |  |  | 0010-296-TIN-0090.pdf
Gidgealpa Gas Satellite - Instrument Air Supply - Instrument Air Package A | GIDG INST AIR 1010-K-004A | 1010-K-004A | Compressor-Air Champion CSF22-GIDG_A012 | Remove the oil element and o-ring using a filter wrench | 3 | M | 4 | 00 |  |  | 0010-296-TIN-0090.pdf
Gidgealpa Gas Satellite - Instrument Air Supply - Instrument Air Package A | GIDG INST AIR 1010-K-004A | 1010-K-004A | Compressor-Air Champion CSF22-GIDG_A041 | Ensure the purge line tube is positioned such that it sits centrally with a maximum clearance of 3mm | 1 | Y | 4 | 00 |  |  | 0010-296-TIN-0092.pdf
Gidgealpa Gas Satellite - Instrument Air Supply - Instrument Air Package A | GIDG INST AIR 1010-K-004A | 1010-K-004A | Compressor-Air Champion CSF22-GIDG_A07 | Close the oil drain valve and replace plug | 3 | M | 4 | 00 |  |  | 0010-296-TIN-0090.pdf
Gidgealpa Gas Satellite - Instrument Air Supply - Instrument Air Package A | GIDG INST AIR 1010-K-004A | 1010-K-004A | Compressor-Air Champion CSF22-GIDG_A06 | Clean the sample point first before removing the plug from the oil drain valve | 3 | M | 4 | 00 |  |  | 0010-296-TIN-0090.pdf
Gidgealpa Gas Satellite - Instrument Air Supply - Instrument Air Package A | GIDG INST AIR 1010-K-004A | 1010-K-004A | Compressor-Air Champion CSF22-GIDG_A045 | Lubricate all moving parts with silicone based o-ring grease | 1 | Y | 4 | 00 |  |  | 0010-296-TIN-0092.pdf
Gidgealpa Gas Satellite - Instrument Air Supply - Instrument Air Package A | GIDG INST AIR 1010-K-004A | 1010-K-004A | Compressor-Air Champion CSF22-GIDG_A039 | Refill the Air-Oil Separator (sump) with new oil until the level reaches the bottom of the oil filler socket. | 1 | Y | 4 | 00 |  |  | 0010-296-TIN-0092.pdf
Gidgealpa Gas Satellite - Instrument Air Supply - Instrument Air Package B | GIDG INST AIR 1010-K-004B | 1010-K-004B | Compressor-Air Champion CSF22-GIDG_A01 | Check the local panel to ensure the unit is opeational and ready to start if in standby mode | 1 | W | 44 | 01 | 1010-K-004B 1W-44-01- | 1010-K-004B 1W-44-01- | OEC Tasks List
Gidgealpa Gas Satellite - Instrument Air Supply - Instrument Air Package B | GIDG INST AIR 1010-KX-004B | 1010-KX-004B | Compressor Package IE-Air Champion CSF22-GIDG_A11 | Inspect all motor air cooling paths to ensure they are clear. Clean as required | 1 | Y | 01 | 00 |  |  | 0010-295-TIN-0003.pdf
Gidgealpa Gas Satellite - Instrument Air Supply - Instrument Air Package B | GIDG INST AIR 1010-KX-004B | 1010-KX-004B | Compressor Package IE-Air Champion CSF22-GIDG_A07 | Inspect solenoid for damage and unauthorized modifications | 1 | Y | 01 | 00 |  |  | 0010-295-TIN-0003.pdf
Gidgealpa Gas Satellite - Instrument Air Supply - Instrument Air Package B | GIDG INST AIR 1010-KX-004B | 1010-KX-004B | Compressor Package IE-Air Champion CSF22-GIDG_A05 | Inspect condition of internal wiring and connections for damage and security | 1 | Y | 01 | 00 |  |  | 0010-295-TIN-0003.pdf
Gidgealpa Gas Satellite - Instrument Air Supply - Instrument Air Package B | GIDG INST AIR 1010-KX-004B | 1010-KX-004B | Compressor Package IE-Air Champion CSF22-GIDG_A13 | Check operation of differential pressure switches | 4 | Y | 01 | 00 |  |  | 0010-295-TIN-0002.pdf
Gidgealpa Gas Satellite - Instrument Air Supply - Instrument Air Package B | GIDG INST AIR 1010-KX-004B | 1010-KX-004B | Compressor Package IE-Air Champion CSF22-GIDG_A14 | Inspect temperature sensor cabling and all connections | 4 | Y | 01 | 00 |  |  | 0010-295-TIN-0002.pdf
Gidgealpa Gas Satellite - Instrument Air Supply - Instrument Air Package B | GIDG INST AIR 1010-KX-004B | 1010-KX-004B | Compressor Package IE-Air Champion CSF22-GIDG_A10 | Check condition of control tubing and small bore fittings | 1 | Y | 01 | 00 |  |  | 0010-295-TIN-0003.pdf
Gidgealpa Gas Satellite - Instrument Air Supply - Instrument Air Package B | GIDG INST AIR 1010-KX-004B | 1010-KX-004B | Compressor Package IE-Air Champion CSF22-GIDG_A04 | Inspect the compressor control panel for damage | 1 | Y | 01 | 00 |  |  | 0010-295-TIN-0003.pdf
Gidgealpa Gas Satellite - Instrument Air Supply - Instrument Air Package B | GIDG INST AIR 1010-KX-004B | 1010-KX-004B | Compressor Package IE-Air Champion CSF22-GIDG_A03 | Inspect condition of all cabling. Ensure all connections are tight | 1 | Y | 01 | 00 |  |  | 0010-295-TIN-0003.pdf
Gidgealpa Gas Satellite - Instrument Air Supply - Instrument Air Package B | GIDG INST AIR 1010-KX-004B | 1010-KX-004B | Compressor Package IE-Air Champion CSF22-GIDG_A15 | Ensure that the high temperature shutdown indicator on the control panel is lit | 4 | Y | 01 | 00 |  |  | 0010-295-TIN-0002.pdf
Gidgealpa Gas Satellite - Instrument Air Supply - Instrument Air Package B | GIDG INST AIR 1010-KX-004B | 1010-KX-004B | Compressor Package IE-Air Champion CSF22-GIDG_A06 | Clean plug connections using contact cleaner | 1 | Y | 01 | 00 |  |  | 0010-295-TIN-0003.pdf
Gidgealpa Gas Satellite - Instrument Air Supply - Instrument Air Package B | GIDG INST AIR 1010-KX-004B | 1010-KX-004B | Compressor Package IE-Air Champion CSF22-GIDG_A12 | Inspect motor frame for signs of cracking especially in the motor mounting areas | 1 | Y | 01 | 00 |  |  | 0010-295-TIN-0003.pdf
Gidgealpa Gas Satellite - Instrument Air Supply - Instrument Air Package B | GIDG INST AIR 1010-KX-004B | 1010-KX-004B | Compressor Package IE-Air Champion CSF22-GIDG_A01 | Inspect switches for damage and unauthorized modifications | 1 | Y | 01 | 00 |  |  | 0010-295-TIN-0003.pdf
Gidgealpa Gas Satellite - Instrument Air Supply - Instrument Air Package B | GIDG INST AIR 1010-KX-004B | 1010-KX-004B | Compressor Package IE-Air Champion CSF22-GIDG_A02 | Inspect condition of all tube work, checking for leaks | 1 | Y | 01 | 00 |  |  | 0010-295-TIN-0003.pdf
Gidgealpa Gas Satellite - Instrument Air Supply - Instrument Air Package B | GIDG INST AIR 1010-KX-004B | 1010-KX-004B | Compressor Package IE-Air Champion CSF22-GIDG_A09 | Inspect Motor for damage and unauthorized modifications | 1 | Y | 01 | 00 |  |  | 0010-295-TIN-0003.pdf
Gidgealpa Gas Satellite - Instrument Air Supply - Instrument Air Package B | GIDG INST AIR 1010-KX-004B | 1010-KX-004B | Compressor Package IE-Air Champion CSF22-GIDG_A08 | Check condition and serviceability of the Motor | 1 | Y | 01 | 00 |  |  | 0010-295-TIN-0003.pdf
Gidgealpa Gas Satellite - Instrument Air Supply - Instrument Air Package B | GIDG INST AIR 1010-K-004B | 1010-K-004B | Compressor-Air Champion CSF22-GIDG_A07 | Close the oil drain valve and replace plug | 3 | M | 4 | 00 |  |  | 0010-296-TIN-0090.pdf
Gidgealpa Gas Satellite - Instrument Air Supply - Instrument Air Package B | GIDG INST AIR 1010-K-004B | 1010-K-004B | Compressor-Air Champion CSF22-GIDG_A036 | Check oil level and top up if necessary | 3 | M | 4 | 00 |  |  | 0010-296-TIN-0090.pdf
Gidgealpa Gas Satellite - Instrument Air Supply - Instrument Air Package B | GIDG INST AIR 1010-K-004B | 1010-K-004B | Compressor-Air Champion CSF22-GIDG_A04 | Check lube oil level and top-up if necessary | 1 | W | 44 | 01 | 1010-K-004B 1W-44-01- | 1010-K-004B 1W-44-01- | OEC Tasks List
Gidgealpa Gas Satellite - Instrument Air Supply - Instrument Air Package B | GIDG INST AIR 1010-K-004B | 1010-K-004B | Compressor-Air Champion CSF22-GIDG_A011 | Inspect purge filter, clean if required | 3 | M | 4 | 00 |  |  | 0010-296-TIN-0090.pdf
Gidgealpa Gas Satellite - Instrument Air Supply - Instrument Air Package B | GIDG INST AIR 1010-K-004B | 1010-K-004B | Compressor-Air Champion CSF22-GIDG_A09 | Remove the oil filler cap and refill the Air-Oil Separator (sump) as required | 3 | M | 4 | 00 |  |  | 0010-296-TIN-0090.pdf
Gidgealpa Gas Satellite - Instrument Air Supply - Instrument Air Package B | GIDG INST AIR 1010-K-004B | 1010-K-004B | Compressor-Air Champion CSF22-GIDG_A010 | Replace the oil filler cap and ensure that the O-ring is properly seated | 3 | M | 4 | 00 |  |  | 0010-296-TIN-0090.pdf
Gidgealpa Gas Satellite - Instrument Air Supply - Instrument Air Package B | GIDG INST AIR 1010-K-004B | 1010-K-004B | Compressor-Air Champion CSF22-GIDG_A012 | Remove the oil element and o-ring using a filter wrench | 3 | M | 4 | 00 |  |  | 0010-296-TIN-0090.pdf
Gidgealpa Gas Satellite - Instrument Air Supply - Instrument Air Package B | GIDG INST AIR 1010-K-004B | 1010-K-004B | Compressor-Air Champion CSF22-GIDG_A06 | Clean the sample point first before removing the plug from the oil drain valve | 3 | M | 4 | 00 |  |  | 0010-296-TIN-0090.pdf
Gidgealpa Gas Satellite - Instrument Air Supply - Instrument Air Package B | GIDG INST AIR 1010-K-004B | 1010-K-004B | Compressor-Air Champion CSF22-GIDG_A039 | Refill the Air-Oil Separator (sump) with new oil until the level reaches the bottom of the oil filler socket. | 1 | Y | 4 | 00 |  |  | 0010-296-TIN-0092.pdf
Gidgealpa Gas Satellite - Instrument Air Supply - Instrument Air Package B | GIDG INST AIR 1010-K-004B | 1010-K-004B | Compressor-Air Champion CSF22-GIDG_A014 | Apply a light film of compressor oil to the new o-ring | 3 | M | 4 | 00 |  |  | 0010-296-TIN-0090.pdf
Gidgealpa Gas Satellite - Instrument Air Supply - Instrument Air Package B | GIDG INST AIR 1010-K-004B | 1010-K-004B | Compressor-Air Champion CSF22-GIDG_A041 | Ensure the purge line tube is positioned such that it sits centrally with a maximum clearance of 3mm | 1 | Y | 4 | 00 |  |  | 0010-296-TIN-0092.pdf
Gidgealpa Gas Satellite - Instrument Air Supply - Instrument Air Package B | GIDG INST AIR 1010-K-004B | 1010-K-004B | Compressor-Air Champion CSF22-GIDG_A05 | Take an oil sample, after shutting down | 3 | M | 4 | 00 |  |  | 0010-296-TIN-0090.pdf
Gidgealpa Gas Satellite - Instrument Air Supply - Instrument Air Package B | GIDG INST AIR 1010-K-004B | 1010-K-004B | Compressor-Air Champion CSF22-GIDG_A08 | Ensure oil analysis label is attached to sample bottle and record compressor run hours | 3 | M | 4 | 00 |  |  | 0010-296-TIN-0090.pdf
Gidgealpa Gas Satellite - Instrument Air Supply - Instrument Air Package B | GIDG INST AIR 1010-K-004B | 1010-K-004B | Compressor-Air Champion CSF22-GIDG_A045 | Lubricate all moving parts with silicone based o-ring grease | 1 | Y | 4 | 00 |  |  | 0010-296-TIN-0092.pdf
Gidgealpa Gas Satellite - Instrument Air Supply - Instrument Air Package B | GIDG INST AIR 1010-K-004B | 1010-K-004B | Compressor-Air Champion CSF22-GIDG_A042 | Replace purge filter element | 1 | Y | 4 | 00 |  |  | 0010-296-TIN-0092.pdf
Gidgealpa Gas Satellite - Instrument Air Supply - Instrument Air Package B | GIDG INST AIR 1010-K-004B | 1010-K-004B | Compressor-Air Champion CSF22-GIDG_A046 | Inspect the compressor rotors for excessive scoring or damage | 1 | Y | 4 | 00 |  |  | 0010-296-TIN-0092.pdf
Gidgealpa Gas Satellite - Instrument Air Supply - Instrument Air Package B | GIDG INST AIR 1010-K-004B | 1010-K-004B | Compressor-Air Champion CSF22-GIDG_A053 | Replace thermostat, slide, and seal using repair kit | 1 | Y | 4 | 00 |  |  | 0010-296-TIN-0092.pdf
Gidgealpa Gas Satellite - Instrument Air Supply - Instrument Air Package B | GIDG INST AIR 1010-K-004B | 1010-K-004B | Compressor-Air Champion CSF22-GIDG_A044 | Replace valve plate, piston, cup seal and 3 x o-rings using seal repair kit | 1 | Y | 4 | 00 |  |  | 0010-296-TIN-0092.pdf
Gidgealpa Gas Satellite - Instrument Air Supply - Instrument Air Package B | GIDG INST AIR 1010-K-004B | 1010-K-004B | Compressor-Air Champion CSF22-GIDG_A051 | Replace seal, check spring, piston spring, o-ring and screws using repair kit | 1 | Y | 4 | 00 |  |  | 0010-296-TIN-0092.pdf
Gidgealpa Gas Satellite - Instrument Air Supply - Instrument Air Package B | GIDG INST AIR 1010-K-004B | 1010-K-004B | Compressor-Air Champion CSF22-GIDG_A030 | Check parallel alignment of pulleys and belts following pulley replacement and/or belt replacement | 3 | M | 4 | 00 |  |  | 0010-296-TIN-0090.pdf
Gidgealpa Gas Satellite - Instrument Air Supply - Instrument Air Package B | GIDG INST AIR 1010-K-004B | 1010-K-004B | Compressor-Air Champion CSF22-GIDG_A021 | Replace the housing cover, ensuring both clips are correctly located and secured | 3 | M | 4 | 00 |  |  | 0010-296-TIN-0090.pdf
Gidgealpa Gas Satellite - Instrument Air Supply - Instrument Air Package B | GIDG INST AIR 1010-K-004B | 1010-K-004B | Compressor-Air Champion CSF22-GIDG_A016 | Clean the exterior of the air filter cover | 3 | M | 4 | 00 |  |  | 0010-296-TIN-0090.pdf
Gidgealpa Gas Satellite - Instrument Air Supply - Instrument Air Package B | GIDG INST AIR 1010-K-004B | 1010-K-004B | Compressor-Air Champion CSF22-GIDG_A017 | Remove air filter cover by pressing the quick release clips | 3 | M | 4 | 00 |  |  | 0010-296-TIN-0090.pdf
Gidgealpa Gas Satellite - Instrument Air Supply - Instrument Air Package B | GIDG INST AIR 1010-K-004B | 1010-K-004B | Compressor-Air Champion CSF22-GIDG_A015 | Hand-tighten the new element until the o-ring is seated and tighten an additional 1/2 to 3/4 of a turn | 3 | M | 4 | 00 |  |  | 0010-296-TIN-0090.pdf
Gidgealpa Gas Satellite - Instrument Air Supply - Instrument Air Package B | GIDG INST AIR 1010-K-004B | 1010-K-004B | Compressor-Air Champion CSF22-GIDG_A020 | Inspect the condition and serviceability of the Air Inlet Filter element, replace as required | 3 | M | 4 | 00 |  |  | 0010-296-TIN-0090.pdf
Gidgealpa Gas Satellite - Instrument Air Supply - Instrument Air Package B | GIDG INST AIR 1010-K-004B | 1010-K-004B | Compressor-Air Champion CSF22-GIDG_A038 | Re-fit compressor cabinet panels | 3 | M | 4 | 00 |  |  | 0010-296-TIN-0090.pdf
Gidgealpa Gas Satellite - Instrument Air Supply - Instrument Air Package B | GIDG INST AIR 1010-K-004B | 1010-K-004B | Compressor-Air Champion CSF22-GIDG_A013 | Clean the o-ring seating surface | 3 | M | 4 | 00 |  |  | 0010-296-TIN-0090.pdf
Gidgealpa Gas Satellite - Instrument Air Supply - Instrument Air Package B | GIDG INST AIR 1010-K-004B | 1010-K-004B | Compressor-Air Champion CSF22-GIDG_A062 | Inspect fan hub is centred within the cowling. adjust & clean as required | 1 | Y | 4 | 00 |  |  | 0010-296-TIN-0092.pdf
Gidgealpa Gas Satellite - Instrument Air Supply - Instrument Air Package B | GIDG INST AIR 1010-K-004B | 1010-K-004B | Compressor-Air Champion CSF22-GIDG_A065 | Clean down compressor package on completion of service, if required | 1 | Y | 4 | 00 |  |  | 0010-296-TIN-0092.pdf
Gidgealpa Gas Satellite - Instrument Air Supply - Instrument Air Package B | GIDG INST AIR 1010-K-004B | 1010-K-004B | Compressor-Air Champion CSF22-GIDG_A018 | Remove air filter element by gently easing it downwards | 3 | M | 4 | 00 |  |  | 0010-296-TIN-0090.pdf
Gidgealpa Gas Satellite - Instrument Air Supply - Instrument Air Package B | GIDG INST AIR 1010-K-004B | 1010-K-004B | Compressor-Air Champion CSF22-GIDG_A019 | Clean the base and interior of the air filter cover using a damp cloth | 3 | M | 4 | 00 |  |  | 0010-296-TIN-0090.pdf
Gidgealpa Gas Satellite - Instrument Air Supply - Instrument Air Package B | GIDG INST AIR 1010-K-004B | 1010-K-004B | Compressor-Air Champion CSF22-GIDG_A047 | Re-fit intake controller assembly to air end | 1 | Y | 4 | 00 |  |  | 0010-296-TIN-0092.pdf
Gidgealpa Gas Satellite - Instrument Air Supply - Instrument Air Package B | GIDG INST AIR 1010-K-004B | 1010-K-004B | Compressor-Air Champion CSF22-GIDG_A040 | Replace with a new separator element and gasket assembly & reassemble filter assembly | 1 | Y | 4 | 00 |  |  | 0010-296-TIN-0092.pdf
Gidgealpa Gas Satellite - Instrument Air Supply - Instrument Air Package B | GIDG INST AIR 1010-K-004B | 1010-K-004B | Compressor-Air Champion CSF22-GIDG_A059 | Remove existing belts | 1 | Y | 4 | 00 |  |  | 0010-296-TIN-0092.pdf
Gidgealpa Gas Satellite - Instrument Air Supply - Instrument Air Package B | GIDG INST AIR 1010-K-004B | 1010-K-004B | Compressor-Air Champion CSF22-GIDG_A048 | Replace the gasket between the inlet control valve and the air end | 1 | Y | 4 | 00 |  |  | 0010-296-TIN-0092.pdf
Gidgealpa Gas Satellite - Instrument Air Supply - Instrument Air Package B | GIDG INST AIR 1010-K-004B | 1010-K-004B | Compressor-Air Champion CSF22-GIDG_A052 | Check the condition of the valve plate, housing and stem, remove any burrs and replace if necessary | 1 | Y | 4 | 00 |  |  | 0010-296-TIN-0092.pdf | 001
Gidgealpa Gas Satellite - Instrument Air Supply - Instrument Air Package B | GIDG INST AIR 1010-K-004B | 1010-K-004B | Compressor-Air Champion CSF22-GIDG_A033 | Inspect pre-filter mat fitted to the front cabinet panel | 3 | M | 4 | 00 |  |  | 0010-296-TIN-0090.pdf | 001
Gidgealpa Gas Satellite - Instrument Air Supply - Instrument Air Package B | GIDG INST AIR 1010-K-004B | 1010-K-004B | Compressor-Air Champion CSF22-GIDG_A032 | Clean out compressor cabinet and remove dirt and grime from components | 3 | M | 4 | 00 |  |  | 0010-296-TIN-0090.pdf
Gidgealpa Gas Satellite - Instrument Air Supply - Instrument Air Package B | GIDG INST AIR 1010-K-004B | 1010-K-004B | Compressor-Air Champion CSF22-GIDG_A031 | Check that the rear face of the airend pulley is positioned 10mm off the mounting face | 3 | M | 4 | 00 |  |  | 0010-296-TIN-0090.pdf
Gidgealpa Gas Satellite - Instrument Air Supply - Instrument Air Package B | GIDG INST AIR 1010-K-004B | 1010-K-004B | Compressor-Air Champion CSF22-GIDG_A037 | Re-tension the separator bolts to 77 Nm (57ft.lbs). | 3 | M | 4 | 00 |  |  | 0010-296-TIN-0090.pdf
Gidgealpa Gas Satellite - Instrument Air Supply - Instrument Air Package B | GIDG INST AIR 1010-K-004B | 1010-K-004B | Compressor-Air Champion CSF22-GIDG_A043 | Overhaul intake control valve | 1 | Y | 4 | 00 |  |  | 0010-296-TIN-0092.pdf
Gidgealpa Gas Satellite - Instrument Air Supply - Instrument Air Package B | GIDG INST AIR 1010-K-004B | 1010-K-004B | Compressor-Air Champion CSF22-GIDG_A054 | Refit to thermo-valve body and replace plug | 1 | Y | 4 | 00 |  |  | 0010-296-TIN-0092.pdf
Gidgealpa Gas Satellite - Instrument Air Supply - Instrument Air Package B | GIDG INST AIR 1010-K-004B | 1010-K-004B | Compressor-Air Champion CSF22-GIDG_A028 | Inspect taper lock bushes and file off burrs, replace if required. | 3 | M | 4 | 00 |  |  | 0010-296-TIN-0090.pdf
Gidgealpa Gas Satellite - Instrument Air Supply - Instrument Air Package B | GIDG INST AIR 1010-K-004B | 1010-K-004B | Compressor-Air Champion CSF22-GIDG_A023 | Remove the belt guard and inspect the condition and serviceability of the vee belts, replace all belts | 3 | M | 4 | 00 |  |  | 0010-296-TIN-0090.pdf
Gidgealpa Gas Satellite - Instrument Air Supply - Instrument Air Package B | GIDG INST AIR 1010-K-004B | 1010-K-004B | Compressor-Air Champion CSF22-GIDG_A026 | Remove tension in existing belts | 3 | M | 4 | 00 |  |  | 0010-296-TIN-0090.pdf
Gidgealpa Gas Satellite - Instrument Air Supply - Instrument Air Package B | GIDG INST AIR 1010-K-004B | 1010-K-004B | Compressor-Air Champion CSF22-GIDG_A02 | Check Belts for tension, noise and wear. Raise WO to rectify as needed | 1 | W | 44 | 01 | 1010-K-004B 1W-44-01- | 1010-K-004B 1W-44-01- | OEC Tasks List
Gidgealpa Gas Satellite - Instrument Air Supply - Instrument Air Package B | GIDG INST AIR 1010-K-004B | 1010-K-004B | Compressor-Air Champion CSF22-GIDG_A063 | Replace pre-filter mat fitted to the front cabinet panel with new | 1 | Y | 4 | 00 |  |  | 0010-296-TIN-0092.pdf
Gidgealpa Gas Satellite - Instrument Air Supply - Instrument Air Package B | GIDG INST AIR 1010-K-004B | 1010-K-004B | Compressor-Air Champion CSF22-GIDG_A055 | Reassemble MPV assembly | 1 | Y | 4 | 00 |  |  | 0010-296-TIN-0092.pdf
Gidgealpa Gas Satellite - Instrument Air Supply - Instrument Air Package B | GIDG INST AIR 1010-K-004B | 1010-K-004B | Compressor-Air Champion CSF22-GIDG_A060 | Inspect pulleys for contamination and clean as required | 1 | Y | 4 | 00 |  |  | 0010-296-TIN-0092.pdf
Gidgealpa Gas Satellite - Instrument Air Supply - Instrument Air Package B | GIDG INST AIR 1010-K-004B | 1010-K-004B | Compressor-Air Champion CSF22-GIDG_A034 | Check all nuts, bolts and pipe fittings are tight | 3 | M | 4 | 00 |  |  | 0010-296-TIN-0090.pdf
Gidgealpa Gas Satellite - Instrument Air Supply - Instrument Air Package B | GIDG INST AIR 1010-K-004B | 1010-K-004B | Compressor-Air Champion CSF22-GIDG_A066 | Check for leaks in all plumbing, tube work and filter seals | 1 | Y | 4 | 00 |  |  | 0010-296-TIN-0092.pdf | 001
Gidgealpa Gas Satellite - Instrument Air Supply - Instrument Air Package B | GIDG INST AIR 1010-K-004B | 1010-K-004B | Compressor-Air Champion CSF22-GIDG_A058 | Replace flexible hosing, and clamps | 1 | Y | 4 | 00 |  |  | 0010-296-TIN-0092.pdf
Gidgealpa Gas Satellite - Instrument Air Supply - Instrument Air Package B | GIDG INST AIR 1010-K-004B | 1010-K-004B | Compressor-Air Champion CSF22-GIDG_A022 | Replace flexible hosing and clamps | 3 | M | 4 | 00 |  |  | 0010-296-TIN-0090.pdf
Gidgealpa Gas Satellite - Instrument Air Supply - Instrument Air Package B | GIDG INST AIR 1010-K-004B | 1010-K-004B | Compressor-Air Champion CSF22-GIDG_A03 | Check inside the enclosure for leaks or other faults | 1 | W | 44 | 01 | 1010-K-004B 1W-44-01- | 1010-K-004B 1W-44-01- | OEC Tasks List
Gidgealpa Gas Satellite - Instrument Air Supply - Instrument Air Package B | GIDG INST AIR 1010-K-004B | 1010-K-004B | Compressor-Air Champion CSF22-GIDG_A050 | Re-connect air intake plumbing | 1 | Y | 4 | 00 |  |  | 0010-296-TIN-0092.pdf
Gidgealpa Gas Satellite - Instrument Air Supply - Instrument Air Package B | GIDG INST AIR 1010-K-004B | 1010-K-004B | Compressor-Air Champion CSF22-GIDG_A029 | Recheck the belt tension FIVE minutes after a new set of belts are fitted and then again TEN minutes later, re-tension as required | 3 | M | 4 | 00 |  |  | 0010-296-TIN-0090.pdf
Gidgealpa Gas Satellite - Instrument Air Supply - Instrument Air Package B | GIDG INST AIR 1010-K-004B | 1010-K-004B | Compressor-Air Champion CSF22-GIDG_A025 | Re-fit belt guard | 3 | M | 4 | 00 |  |  | 0010-296-TIN-0090.pdf
Gidgealpa Gas Satellite - Instrument Air Supply - Instrument Air Package B | GIDG INST AIR 1010-K-004B | 1010-K-004B | Compressor-Air Champion CSF22-GIDG_A024 | Re-tension belts as required by tightening the tensioning | 3 | M | 4 | 00 |  |  | 0010-296-TIN-0090.pdf
Gidgealpa Gas Satellite - Instrument Air Supply - Instrument Air Package B | GIDG INST AIR 1010-K-004B | 1010-K-004B | Compressor-Air Champion CSF22-GIDG_A027 | Inspect pulley profile for excessive wear, Replace motor and airend pulleys as required. | 3 | M | 4 | 00 |  |  | 0010-296-TIN-0090.pdf
Gidgealpa Gas Satellite - Instrument Air Supply - Instrument Air Package B | GIDG INST AIR 1010-K-004B | 1010-K-004B | Compressor-Air Champion CSF22-GIDG_A035 | Lubricate electric motor bearings | 3 | M | 4 | 00 |  |  | 0010-296-TIN-0090.pdf
Gidgealpa Gas Satellite - Instrument Air Supply - Instrument Air Package B | GIDG INST AIR 1010-K-004B | 1010-K-004B | Compressor-Air Champion CSF22-GIDG_A064 | Inspect all motor air cooling paths to ensure they are clear | 1 | Y | 4 | 00 |  |  | 0010-296-TIN-0092.pdf
Gidgealpa Gas Satellite - Instrument Air Supply - Instrument Air Package B | GIDG INST AIR 1010-K-004B | 1010-K-004B | Compressor-Air Champion CSF22-GIDG_A049 | Replace VMC style inlet controller | 1 | Y | 4 | 00 |  |  | 0010-296-TIN-0092.pdf
Gidgealpa Gas Satellite - Liquids Handling - Condensate Pump Package A | GIDG LIQ 1010-EM-001A | 1010-EM-001A | Motor-Pump Toshiba-GIDG_A09 | Re-grease motor bearings | 12 | M | 01 | 00 |  |  | 2219071.docx
Gidgealpa Gas Satellite - Liquids Handling - Condensate Pump Package A | GIDG LIQ 1010-P-001A | 1010-P-001A | Pump-Condensate Duraqual PF1253-GIDG_A022 | Inspect condition of drive pulley grooves with pulley groove gauge | 1 | Y | 4 | 00 |  |  | 2220246.docx
Gidgealpa Gas Satellite - Liquids Handling - Condensate Pump Package A | GIDG LIQ 1010-P-001A | 1010-P-001A | Pump-Condensate Duraqual PF1253-GIDG_A021 | Replace drive belts and re-tension | 1 | Y | 4 | 00 |  |  | 2220246.docx
Gidgealpa Gas Satellite - Liquids Handling - Condensate Pump Package A | GIDG LIQ 1010-EM-001A | 1010-EM-001A | Motor-Pump Toshiba-GIDG_A03 | Inspect condition of 3 phase and control cables and lugs for deterioration, overheating and support in terminal box | 12 | M | 01 | 00 |  |  | 2219071.docx
Gidgealpa Gas Satellite - Liquids Handling - Condensate Pump Package A | GIDG LIQ 1010-EM-001A | 1010-EM-001A | Motor-Pump Toshiba-GIDG_A08 | Install terminal box covers | 12 | M | 01 | 00 |  |  | 2219071.docx
Gidgealpa Gas Satellite - Liquids Handling - Condensate Pump Package A | GIDG LIQ 1010-EM-001A | 1010-EM-001A | Motor-Pump Toshiba-GIDG_A010 | Clean the grease drain of purged grease, inspect purged grease for evidence of metal particles or contamination and replace the drain plug | 12 | M | 01 | 00 |  |  | 2219071.docx
Gidgealpa Gas Satellite - Liquids Handling - Condensate Pump Package A | GIDG LIQ 1010-P-001A | 1010-P-001A | Pump-Condensate Duraqual PF1253-GIDG_A016 | Check belt tension | 6 | M | 4 | 00 |  |  | 2218663.docx
Gidgealpa Gas Satellite - Liquids Handling - Condensate Pump Package A | GIDG LIQ 1010-P-001A | 1010-P-001A | Pump-Condensate Duraqual PF1253-GIDG_A034 | Ensure the isolation manifold valves are set to the service position | 1 | Y | 01 | 00 |  |  | 2220763.docx
Gidgealpa Gas Satellite - Liquids Handling - Condensate Pump Package A | GIDG LIQ 1010-P-001A | 1010-P-001A | Pump-Condensate Duraqual PF1253-GIDG_A030 | Overhaul pressure switch | 1 | Y | 01 | 00 |  |  | 2220763.docx
Gidgealpa Gas Satellite - Liquids Handling - Condensate Pump Package A | GIDG LIQ 1010-P-001A | 1010-P-001A | Pump-Condensate Duraqual PF1253-GIDG_A031 | Calibrate Pressure Switch | 1 | Y | 01 | 00 |  |  | 2220763.docx
Gidgealpa Gas Satellite - Liquids Handling - Condensate Pump Package A | GIDG LIQ 1010-P-001A | 1010-P-001A | Pump-Condensate Duraqual PF1253-GIDG_A05 | Blow down all sight glasses & level controllers as required | 1 | M | 44 | 01 | 1010-P-001A 1M-44-01- | 1010-P-001A 1M-44-01- | OEC Tasks List
Gidgealpa Gas Satellite - Liquids Handling - Condensate Pump Package A | GIDG LIQ 1010-P-001A | 1010-P-001A | Pump-Condensate Duraqual PF1253-GIDG_A028 | Remove Pressure Switch to workshop | 1 | Y | 01 | 00 |  |  | 2220763.docx
Gidgealpa Gas Satellite - Liquids Handling - Condensate Pump Package A | GIDG LIQ 1010-P-001A | 1010-P-001A | Pump-Condensate Duraqual PF1253-GIDG_A03 | Check liquid / interface levels in sight glasses on the condensate drum | 1 | W | 44 | 01 | 1010-P-001A 1W-44-01- | 1010-P-001A 1W-44-01- | OEC Tasks List
Gidgealpa Gas Satellite - Liquids Handling - Condensate Pump Package A | GIDG LIQ 1010-P-001A | 1010-P-001A | Pump-Condensate Duraqual PF1253-GIDG_A029 | Inspect sensing lines for deposits. | 1 | Y | 01 | 00 |  |  | 2220763.docx
Gidgealpa Gas Satellite - Liquids Handling - Condensate Pump Package A | GIDG LIQ 1010-P-001A | 1010-P-001A | Pump-Condensate Duraqual PF1253-GIDG_A04 | Ensure sight glasses are clean and operational | 1 | D | 44 | 01 | 1010-P-001A 1D-44-01- | 1010-P-001A 1D-44-01- | OEC Tasks List
Gidgealpa Gas Satellite - Liquids Handling - Condensate Pump Package A | GIDG LIQ 1010-P-001A | 1010-P-001A | Pump-Condensate Duraqual PF1253-GIDG_A026 | Overhaul condensate pump high discharge pressure switch | 1 | Y | 01 | 00 |  |  | 2220763.docx | 001
Gidgealpa Gas Satellite - Liquids Handling - Condensate Pump Package A | GIDG LIQ 1010-P-001A | 1010-P-001A | Pump-Condensate Duraqual PF1253-GIDG_A06 | Check gland packing on pumps and report if there is a fault | 1 | M | 44 | 01 | 1010-P-001A 1M-44-01- | 1010-P-001A 1M-44-01- | OEC Tasks List
Gidgealpa Gas Satellite - Liquids Handling - Condensate Pump Package A | GIDG LIQ 1010-P-001A | 1010-P-001A | Pump-Condensate Duraqual PF1253-GIDG_A09 | For Liquids Recovery Pump, Check for leaks | 1 | W | 44 | 01 | 1010-P-001A 1W-44-01-001 | 1010-P-001A 1W-44-01-001 | OEC Tasks List | 001
Gidgealpa Gas Satellite - Liquids Handling - Condensate Pump Package A | GIDG LIQ 1010-P-001A | 1010-P-001A | Pump-Condensate Duraqual PF1253-GIDG_A033 | Ensure impulse lines are filled with the correct medium | 1 | Y | 01 | 00 |  |  | 2220763.docx | 001
Gidgealpa Gas Satellite - Liquids Handling - Condensate Pump Package A | GIDG LIQ 1010-P-001A | 1010-P-001A | Pump-Condensate Duraqual PF1253-GIDG_A018 | Check pump foundation bolts are tight | 1 | Y | 4 | 00 |  |  | 2220246.docx
Gidgealpa Gas Satellite - Liquids Handling - Condensate Pump Package A | GIDG LIQ 1010-P-001A | 1010-P-001A | Pump-Condensate Duraqual PF1253-GIDG_A010 | For Liquids Recovery Pump, Check oil levels and top up as required | 1 | W | 44 | 01 | 1010-P-001A 1W-44-01- | 1010-P-001A 1W-44-01- | OEC Tasks List
Gidgealpa Gas Satellite - Liquids Handling - Condensate Pump Package A | GIDG LIQ 1010-P-001A | 1010-P-001A | Pump-Condensate Duraqual PF1253-GIDG_A01 | Ensure the condensate pumps are fully operational | 1 | W | 44 | 01 | 1010-P-001A 1W-44-01- | 1010-P-001A 1W-44-01- | OEC Tasks List
Gidgealpa Gas Satellite - Liquids Handling - Condensate Pump Package A | GIDG LIQ 1010-P-001A | 1010-P-001A | Pump-Condensate Duraqual PF1253-GIDG_A032 | Check tightness of impulse line supports | 1 | Y | 01 | 00 |  |  | 2220763.docx
Gidgealpa Gas Satellite - Liquids Handling - Condensate Pump Package A | GIDG LIQ 1010-P-001A | 1010-P-001A | Pump-Condensate Duraqual PF1253-GIDG_A015 | Check pulsation damper pre-charge pressure | 6 | M | 4 | 00 |  |  | 2218663.docx
Gidgealpa Gas Satellite - Liquids Handling - Condensate Pump Package A | GIDG LIQ 1010-P-001A | 1010-P-001A | Pump-Condensate Duraqual PF1253-GIDG_A017 | Check motor hold down bolts are tight | 1 | Y | 4 | 00 |  |  | 2220246.docx
Gidgealpa Gas Satellite - Liquids Handling - Condensate Pump Package A | GIDG LIQ 1010-P-001A | 1010-P-001A | Pump-Condensate Duraqual PF1253-GIDG_A027 | Inspect tube work for visible signs of wear | 1 | Y | 01 | 00 |  |  | 2220763.docx
Gidgealpa Gas Satellite - Liquids Handling - Condensate Pump Package A | GIDG LIQ 1010-P-001A | 1010-P-001A | Pump-Condensate Duraqual PF1253-GIDG_A02 | Check vessel and associated pipework for leaks | 1 | W | 44 | 01 | 1010-P-001A 1W-44-01- | 1010-P-001A 1W-44-01- | OEC Tasks List
Gidgealpa Gas Satellite - Liquids Handling - Condensate Pump Package A | GIDG LIQ 1010-P-001A | 1010-P-001A | Pump-Condensate Duraqual PF1253-GIDG_A019 | Clean pump crankcase oil leveller of sludge | 1 | Y | 4 | 00 |  |  | 2220246.docx
Gidgealpa Gas Satellite - Liquids Handling - Condensate Pump Package A | GIDG LIQ 1010-P-001A | 1010-P-001A | Pump-Condensate Duraqual PF1253-GIDG_A014 | Remove pump crankcase breather and clean with a non-explosive solvent | 6 | M | 4 | 00 |  |  | 2218663.docx
Gidgealpa Gas Satellite - Liquids Handling - Condensate Pump Package A | GIDG LIQ 1010-P-001A | 1010-P-001A | Pump-Condensate Duraqual PF1253-GIDG_A020 | Ensure leveller is repositioned for correct crankcase oil level | 1 | Y | 4 | 00 |  |  | 2220246.docx
Gidgealpa Gas Satellite - Liquids Handling - Condensate Pump Package A | GIDG LIQ 1010-P-001A | 1010-P-001A | Pump-Condensate Duraqual PF1253-GIDG_A024 | Check pump pony rod for scoring | 1 | Y | 4 | 00 |  |  | 2220246.docx | 001
Gidgealpa Gas Satellite - Liquids Handling - Condensate Pump Package A | GIDG LIQ 1010-P-001A | 1010-P-001A | Pump-Condensate Duraqual PF1253-GIDG_A023 | Check pump plungers for scoring | 1 | Y | 4 | 00 |  |  | 2220246.docx
Gidgealpa Gas Satellite - Liquids Handling - Condensate Pump Package A | GIDG LIQ 1010-P-001A | 1010-P-001A | Pump-Condensate Duraqual PF1253-GIDG_A025 | Remove and replace NRV | 1 | Y | 4 | 00 |  |  | 2220246.docx
Gidgealpa Gas Satellite - Liquids Handling - Condensate Pump Package A | GIDG LIQ 1010-P-001A | 1010-P-001A | Pump-Condensate Duraqual PF1253-GIDG_A012 | Clean sample point first, then run oil from the sample point to ensure the sample isn't contaminated | 6 | M | 4 | 00 |  |  | 2218663.docx
Gidgealpa Gas Satellite - Liquids Handling - Condensate Pump Package A | GIDG LIQ 1010-P-001A | 1010-P-001A | Pump-Condensate Duraqual PF1253-GIDG_A013 | Replace pump lube oil filter using filter strap | 6 | M | 4 | 00 |  |  | 2218663.docx
Gidgealpa Gas Satellite - Liquids Handling - Condensate Pump Package A | GIDG LIQ 1010-P-001A | 1010-P-001A | Pump-Condensate Duraqual PF1253-GIDG_A011 | Take an oil sample | 6 | M | 4 | 00 |  |  | 2218663.docx
Gidgealpa Gas Satellite - Liquids Handling - Condensate Pump Package A | GIDG LIQ 1010-P-001A | 1010-P-001A | Pump-Condensate Duraqual PF1253-GIDG_A08 | Top up lubricator header | 1 | M | 44 | 01 | 1010-P-001A 1M-44-01-001 | 1010-P-001A 1M-44-01-001 | OEC Tasks List | 001
Gidgealpa Gas Satellite - Liquids Handling - Condensate Pump Package A | GIDG LIQ 1010-P-001A | 1010-P-001A | Pump-Condensate Duraqual PF1253-GIDG_A07 | Top up crank case oil on all pumps | 1 | M | 44 | 01 | 1010-P-001A 1M-44-01-001 | 1010-P-001A 1M-44-01-001 | OEC Tasks List | 001
Gidgealpa Gas Satellite - Liquids Handling - Condensate Pump Package A | GIDG LIQ 1010-EM-001A | 1010-EM-001A | Motor-Pump Toshiba-GIDG_A07 | Inspect gasket for deterioration and terminal box for contamination | 12 | M | 01 | 00 |  |  | 2219071.docx
Gidgealpa Gas Satellite - Liquids Handling - Condensate Pump Package A | GIDG LIQ 1010-EM-001A | 1010-EM-001A | Motor-Pump Toshiba-GIDG_A02 | Remove terminal box covers | 12 | M | 01 | 00 |  |  | 2219071.docx
Gidgealpa Gas Satellite - Liquids Handling - Condensate Pump Package A | GIDG LIQ 1010-EM-001A | 1010-EM-001A | Motor-Pump Toshiba-GIDG_A04 | Check tightness of all local 3 phase and control terminations | 12 | M | 01 | 00 |  |  | 2219071.docx
Gidgealpa Gas Satellite - Liquids Handling - Condensate Pump Package A | GIDG LIQ 1010-EM-001A | 1010-EM-001A | Motor-Pump Toshiba-GIDG_A01 | Inspect motor for excess dirt and oil build up in particular cooling fan inlet and outlet areas | 12 | M | 01 | 00 |  |  | 2219071.docx
Gidgealpa Gas Satellite - Liquids Handling - Condensate Pump Package A | GIDG LIQ 1010-EM-001A | 1010-EM-001A | Motor-Pump Toshiba-GIDG_A06 | Inspect condition of all earth wiring | 12 | M | 01 | 00 |  |  | 2219071.docx
Gidgealpa Gas Satellite - Liquids Handling - Condensate Pump Package A | GIDG LIQ 1010-EM-001A | 1010-EM-001A | Motor-Pump Toshiba-GIDG_A05 | Check tightness of earth wiring connections | 12 | M | 01 | 00 |  |  | 2219071.docx
Gidgealpa Gas Satellite - Liquids Handling - Condensate Pump Package B | GIDG LIQ 1010-EM-001B | 1010-EM-001B | Motor-Pump Toshiba-GIDG_A010 | Clean the grease drain of purged grease, inspect purged grease for evidence of metal particles or contamination and replace the drain plug | 12 | M | 01 | 00 |  |  | 2219071.docx
Gidgealpa Gas Satellite - Liquids Handling - Condensate Pump Package B | GIDG LIQ 1010-P-001B | 1010-P-001B | Pump-Condensate Duraqual PF1253-GIDG_A07 | Top up crank case oil on all pumps | 1 | M | 44 | 01 | 1010-P-001B 1M-44-01- | 1010-P-001B 1M-44-01- | OEC Tasks List
Gidgealpa Gas Satellite - Liquids Handling - Condensate Pump Package B | GIDG LIQ 1010-P-001B | 1010-P-001B | Pump-Condensate Duraqual PF1253-GIDG_A08 | Top up lubricator header | 1 | M | 44 | 01 | 1010-P-001B 1M-44-01- | 1010-P-001B 1M-44-01- | OEC Tasks List
Gidgealpa Gas Satellite - Liquids Handling - Condensate Pump Package B | GIDG LIQ 1010-P-001B | 1010-P-001B | Pump-Condensate Duraqual PF1253-GIDG_A013 | Replace pump lube oil filter using filter strap | 6 | M | 4 | 00 |  |  | 2218663.docx
Gidgealpa Gas Satellite - Liquids Handling - Condensate Pump Package B | GIDG LIQ 1010-P-001B | 1010-P-001B | Pump-Condensate Duraqual PF1253-GIDG_A011 | Take an oil sample | 6 | M | 4 | 00 |  |  | 2218663.docx
Gidgealpa Gas Satellite - Liquids Handling - Condensate Pump Package B | GIDG LIQ 1010-P-001B | 1010-P-001B | Pump-Condensate Duraqual PF1253-GIDG_A012 | Clean sample point first, then run oil from the sample point to ensure the sample isn't contaminated | 6 | M | 4 | 00 |  |  | 2218663.docx
Gidgealpa Gas Satellite - Liquids Handling - Condensate Pump Package B | GIDG LIQ 1010-P-001B | 1010-P-001B | Pump-Condensate Duraqual PF1253-GIDG_A027 | Inspect tube work for visible signs of wear | 1 | Y | 01 | 00 |  |  | 2220763.docx
Gidgealpa Gas Satellite - Liquids Handling - Condensate Pump Package B | GIDG LIQ 1010-P-001B | 1010-P-001B | Pump-Condensate Duraqual PF1253-GIDG_A02 | Check vessel and associated pipework for leaks | 1 | W | 44 | 01 | 1010-P-001B 1W-44-01- | 1010-P-001B 1W-44-01- | OEC Tasks List
Gidgealpa Gas Satellite - Liquids Handling - Condensate Pump Package B | GIDG LIQ 1010-P-001B | 1010-P-001B | Pump-Condensate Duraqual PF1253-GIDG_A021 | Replace drive belts and re-tension | 1 | Y | 4 | 00 |  |  | 2220246.docx
Gidgealpa Gas Satellite - Liquids Handling - Condensate Pump Package B | GIDG LIQ 1010-P-001B | 1010-P-001B | Pump-Condensate Duraqual PF1253-GIDG_A016 | Check belt tension | 6 | M | 4 | 00 |  |  | 2218663.docx
Gidgealpa Gas Satellite - Liquids Handling - Condensate Pump Package B | GIDG LIQ 1010-P-001B | 1010-P-001B | Pump-Condensate Duraqual PF1253-GIDG_A022 | Inspect condition of drive pulley grooves with pulley groove gauge | 1 | Y | 4 | 00 |  |  | 2220246.docx
Gidgealpa Gas Satellite - Liquids Handling - Condensate Pump Package B | GIDG LIQ 1010-P-001B | 1010-P-001B | Pump-Condensate Duraqual PF1253-GIDG_A024 | Check pump pony rod for scoring | 1 | Y | 4 | 00 |  |  | 2220246.docx
Gidgealpa Gas Satellite - Liquids Handling - Condensate Pump Package B | GIDG LIQ 1010-P-001B | 1010-P-001B | Pump-Condensate Duraqual PF1253-GIDG_A023 | Check pump plungers for scoring | 1 | Y | 4 | 00 |  |  | 2220246.docx
Gidgealpa Gas Satellite - Liquids Handling - Condensate Pump Package B | GIDG LIQ 1010-P-001B | 1010-P-001B | Pump-Condensate Duraqual PF1253-GIDG_A025 | Remove and replace NRV | 1 | Y | 4 | 00 |  |  | 2220246.docx
Gidgealpa Gas Satellite - Liquids Handling - Condensate Pump Package B | GIDG LIQ 1010-P-001B | 1010-P-001B | Pump-Condensate Duraqual PF1253-GIDG_A019 | Clean pump crankcase oil leveller of sludge | 1 | Y | 4 | 00 |  |  | 2220246.docx
Gidgealpa Gas Satellite - Liquids Handling - Condensate Pump Package B | GIDG LIQ 1010-P-001B | 1010-P-001B | Pump-Condensate Duraqual PF1253-GIDG_A020 | Ensure leveller is repositioned for correct crankcase oil level | 1 | Y | 4 | 00 |  |  | 2220246.docx
Gidgealpa Gas Satellite - Liquids Handling - Condensate Pump Package B | GIDG LIQ 1010-P-001B | 1010-P-001B | Pump-Condensate Duraqual PF1253-GIDG_A014 | Remove pump crankcase breather and clean with a non-explosive solvent | 6 | M | 4 | 00 |  |  | 2218663.docx
Gidgealpa Gas Satellite - Liquids Handling - Condensate Pump Package B | GIDG LIQ 1010-P-001B | 1010-P-001B | Pump-Condensate Duraqual PF1253-GIDG_A06 | Check gland packing on pumps and report if there is a fault | 1 | M | 44 | 01 | 1010-P-001B 1M-44-01- | 1010-P-001B 1M-44-01- | OEC Tasks List
Gidgealpa Gas Satellite - Liquids Handling - Condensate Pump Package B | GIDG LIQ 1010-P-001B | 1010-P-001B | Pump-Condensate Duraqual PF1253-GIDG_A01 | Ensure the condensate pumps are fully operational | 1 | W | 44 | 01 | 1010-P-001B 1W-44-01-001 | 1010-P-001B 1W-44-01-001 | OEC Tasks List | 001
Gidgealpa Gas Satellite - Liquids Handling - Condensate Pump Package B | GIDG LIQ 1010-P-001B | 1010-P-001B | Pump-Condensate Duraqual PF1253-GIDG_A018 | Check pump foundation bolts are tight | 1 | Y | 4 | 00 |  |  | 2220246.docx
Gidgealpa Gas Satellite - Liquids Handling - Condensate Pump Package B | GIDG LIQ 1010-P-001B | 1010-P-001B | Pump-Condensate Duraqual PF1253-GIDG_A09 | For Liquids Recovery Pump, Check for leaks | 1 | W | 44 | 01 | 1010-P-001B 1W-44-01- | 1010-P-001B 1W-44-01- | OEC Tasks List
Gidgealpa Gas Satellite - Liquids Handling - Condensate Pump Package B | GIDG LIQ 1010-P-001B | 1010-P-001B | Pump-Condensate Duraqual PF1253-GIDG_A033 | Ensure impulse lines are filled with the correct medium | 1 | Y | 01 | 00 |  |  | 2220763.docx
Gidgealpa Gas Satellite - Liquids Handling - Condensate Pump Package B | GIDG LIQ 1010-P-001B | 1010-P-001B | Pump-Condensate Duraqual PF1253-GIDG_A017 | Check motor hold down bolts are tight | 1 | Y | 4 | 00 |  |  | 2220246.docx
Gidgealpa Gas Satellite - Liquids Handling - Condensate Pump Package B | GIDG LIQ 1010-P-001B | 1010-P-001B | Pump-Condensate Duraqual PF1253-GIDG_A032 | Check tightness of impulse line supports | 1 | Y | 01 | 00 |  |  | 2220763.docx
Gidgealpa Gas Satellite - Liquids Handling - Condensate Pump Package B | GIDG LIQ 1010-P-001B | 1010-P-001B | Pump-Condensate Duraqual PF1253-GIDG_A010 | For Liquids Recovery Pump, Check oil levels and top up as required | 1 | W | 44 | 01 | 1010-P-001B 1W-44-01- | 1010-P-001B 1W-44-01- | OEC Tasks List
Gidgealpa Gas Satellite - Liquids Handling - Condensate Pump Package B | GIDG LIQ 1010-P-001B | 1010-P-001B | Pump-Condensate Duraqual PF1253-GIDG_A015 | Check pulsation damper pre-charge pressure | 6 | M | 4 | 00 |  |  | 2218663.docx
Gidgealpa Gas Satellite - Liquids Handling - Condensate Pump Package B | GIDG LIQ 1010-P-001B | 1010-P-001B | Pump-Condensate Duraqual PF1253-GIDG_A030 | Overhaul pressure switch | 1 | Y | 01 | 00 |  |  | 2220763.docx | 001
Gidgealpa Gas Satellite - Liquids Handling - Condensate Pump Package B | GIDG LIQ 1010-P-001B | 1010-P-001B | Pump-Condensate Duraqual PF1253-GIDG_A05 | Blow down all sight glasses & level controllers as required | 1 | M | 44 | 01 | 1010-P-001B 1M-44-01- | 1010-P-001B 1M-44-01- | OEC Tasks List
Gidgealpa Gas Satellite - Liquids Handling - Condensate Pump Package B | GIDG LIQ 1010-P-001B | 1010-P-001B | Pump-Condensate Duraqual PF1253-GIDG_A029 | Inspect sensing lines for deposits. | 1 | Y | 01 | 00 |  |  | 2220763.docx | 001
Gidgealpa Gas Satellite - Liquids Handling - Condensate Pump Package B | GIDG LIQ 1010-P-001B | 1010-P-001B | Pump-Condensate Duraqual PF1253-GIDG_A031 | Calibrate Pressure Switch | 1 | Y | 01 | 00 |  |  | 2220763.docx
Gidgealpa Gas Satellite - Liquids Handling - Condensate Pump Package B | GIDG LIQ 1010-P-001B | 1010-P-001B | Pump-Condensate Duraqual PF1253-GIDG_A026 | Overhaul condensate pump high discharge pressure switch | 1 | Y | 01 | 00 |  |  | 2220763.docx
Gidgealpa Gas Satellite - Liquids Handling - Condensate Pump Package B | GIDG LIQ 1010-P-001B | 1010-P-001B | Pump-Condensate Duraqual PF1253-GIDG_A028 | Remove Pressure Switch to workshop | 1 | Y | 01 | 00 |  |  | 2220763.docx
Gidgealpa Gas Satellite - Liquids Handling - Condensate Pump Package B | GIDG LIQ 1010-P-001B | 1010-P-001B | Pump-Condensate Duraqual PF1253-GIDG_A04 | Ensure sight glasses are clean and operational | 1 | D | 44 | 01 | 1010-P-001B 1D-44-01- | 1010-P-001B 1D-44-01- | OEC Tasks List
Gidgealpa Gas Satellite - Liquids Handling - Condensate Pump Package B | GIDG LIQ 1010-P-001B | 1010-P-001B | Pump-Condensate Duraqual PF1253-GIDG_A03 | Check liquid / interface levels in sight glasses on the condensate drum | 1 | W | 44 | 01 | 1010-P-001B 1W-44-01- | 1010-P-001B 1W-44-01- | OEC Tasks List
Gidgealpa Gas Satellite - Liquids Handling - Condensate Pump Package B | GIDG LIQ 1010-P-001B | 1010-P-001B | Pump-Condensate Duraqual PF1253-GIDG_A034 | Ensure the isolation manifold valves are set to the service position | 1 | Y | 01 | 00 |  |  | 2220763.docx
Gidgealpa Gas Satellite - Liquids Handling - Condensate Pump Package B | GIDG LIQ 1010-EM-001B | 1010-EM-001B | Motor-Pump Toshiba-GIDG_A07 | Inspect gasket for deterioration and terminal box for contamination | 12 | M | 01 | 00 |  |  | 2219071.docx
Gidgealpa Gas Satellite - Liquids Handling - Condensate Pump Package B | GIDG LIQ 1010-EM-001B | 1010-EM-001B | Motor-Pump Toshiba-GIDG_A04 | Check tightness of all local 3 phase and control terminations | 12 | M | 01 | 00 |  |  | 2219071.docx
Gidgealpa Gas Satellite - Liquids Handling - Condensate Pump Package B | GIDG LIQ 1010-EM-001B | 1010-EM-001B | Motor-Pump Toshiba-GIDG_A02 | Remove terminal box covers | 12 | M | 01 | 00 |  |  | 2219071.docx
Gidgealpa Gas Satellite - Liquids Handling - Condensate Pump Package B | GIDG LIQ 1010-EM-001B | 1010-EM-001B | Motor-Pump Toshiba-GIDG_A03 | Inspect condition of 3 phase and control cables and lugs for deterioration, overheating and support in terminal box | 12 | M | 01 | 00 |  |  | 2219071.docx
Gidgealpa Gas Satellite - Liquids Handling - Condensate Pump Package B | GIDG LIQ 1010-EM-001B | 1010-EM-001B | Motor-Pump Toshiba-GIDG_A08 | Install terminal box covers | 12 | M | 01 | 00 |  |  | 2219071.docx
Gidgealpa Gas Satellite - Liquids Handling - Condensate Pump Package B | GIDG LIQ 1010-EM-001B | 1010-EM-001B | Motor-Pump Toshiba-GIDG_A06 | Inspect condition of all earth wiring | 12 | M | 01 | 00 |  |  | 2219071.docx
Gidgealpa Gas Satellite - Liquids Handling - Condensate Pump Package B | GIDG LIQ 1010-EM-001B | 1010-EM-001B | Motor-Pump Toshiba-GIDG_A05 | Check tightness of earth wiring connections | 12 | M | 01 | 00 |  |  | 2219071.docx
Gidgealpa Gas Satellite - Liquids Handling - Condensate Pump Package B | GIDG LIQ 1010-EM-001B | 1010-EM-001B | Motor-Pump Toshiba-GIDG_A09 | Re-grease motor bearings | 12 | M | 01 | 00 |  |  | 2219071.docx
Gidgealpa Gas Satellite - Liquids Handling - Condensate Pump Package B | GIDG LIQ 1010-EM-001B | 1010-EM-001B | Motor-Pump Toshiba-GIDG_A01 | Inspect motor for excess dirt and oil build up in particular cooling fan inlet and outlet areas | 12 | M | 01 | 00 |  |  | 2219071.docx
Gidgealpa Gas Satellite - Liquids Handling - Condensate Pump Package C | GIDG LIQ 1010-EM-001C | 1010-EM-001C | Motor-Pump Toshiba-GIDG_A010 | Clean the grease drain of purged grease, inspect purged grease for evidence of metal particles or contamination and replace the drain plug | 12 | M | 01 | 00 |  |  | 2219071.docx
Gidgealpa Gas Satellite - Liquids Handling - Condensate Pump Package C | GIDG LIQ 1010-P-001C | 1010-P-001C | Pump-Condensate Duraqual PF1253-GIDG_A022 | Inspect condition of drive pulley grooves with pulley groove gauge | 1 | Y | 4 | 00 |  |  | 2220246.docx
Gidgealpa Gas Satellite - Liquids Handling - Condensate Pump Package C | GIDG LIQ 1010-P-001C | 1010-P-001C | Pump-Condensate Duraqual PF1253-GIDG_A021 | Replace drive belts and re-tension | 1 | Y | 4 | 00 |  |  | 2220246.docx
Gidgealpa Gas Satellite - Liquids Handling - Condensate Pump Package C | GIDG LIQ 1010-P-001C | 1010-P-001C | Pump-Condensate Duraqual PF1253-GIDG_A016 | Check belt tension | 6 | M | 4 | 00 |  |  | 2218663.docx
Gidgealpa Gas Satellite - Liquids Handling - Condensate Pump Package C | GIDG LIQ 1010-P-001C | 1010-P-001C | Pump-Condensate Duraqual PF1253-GIDG_A034 | Ensure the isolation manifold valves are set to the service position | 1 | Y | 01 | 00 |  |  | 2220763.docx
Gidgealpa Gas Satellite - Liquids Handling - Condensate Pump Package C | GIDG LIQ 1010-P-001C | 1010-P-001C | Pump-Condensate Duraqual PF1253-GIDG_A030 | Overhaul pressure switch | 1 | Y | 01 | 00 |  |  | 2220763.docx
Gidgealpa Gas Satellite - Liquids Handling - Condensate Pump Package C | GIDG LIQ 1010-P-001C | 1010-P-001C | Pump-Condensate Duraqual PF1253-GIDG_A031 | Calibrate Pressure Switch | 1 | Y | 01 | 00 |  |  | 2220763.docx
Gidgealpa Gas Satellite - Liquids Handling - Condensate Pump Package C | GIDG LIQ 1010-P-001C | 1010-P-001C | Pump-Condensate Duraqual PF1253-GIDG_A05 | Blow down all sight glasses & level controllers as required | 1 | M | 44 | 01 | 1010-P-001C 1M-44-01- | 1010-P-001C 1M-44-01- | OEC Tasks List
Gidgealpa Gas Satellite - Liquids Handling - Condensate Pump Package C | GIDG LIQ 1010-P-001C | 1010-P-001C | Pump-Condensate Duraqual PF1253-GIDG_A028 | Remove Pressure Switch to workshop | 1 | Y | 01 | 00 |  |  | 2220763.docx
Gidgealpa Gas Satellite - Liquids Handling - Condensate Pump Package C | GIDG LIQ 1010-P-001C | 1010-P-001C | Pump-Condensate Duraqual PF1253-GIDG_A03 | Check liquid / interface levels in sight glasses on the condensate drum | 1 | W | 44 | 01 | 1010-P-001C 1W-44-01- | 1010-P-001C 1W-44-01- | OEC Tasks List
Gidgealpa Gas Satellite - Liquids Handling - Condensate Pump Package C | GIDG LIQ 1010-P-001C | 1010-P-001C | Pump-Condensate Duraqual PF1253-GIDG_A029 | Inspect sensing lines for deposits. | 1 | Y | 01 | 00 |  |  | 2220763.docx
Gidgealpa Gas Satellite - Liquids Handling - Condensate Pump Package C | GIDG LIQ 1010-P-001C | 1010-P-001C | Pump-Condensate Duraqual PF1253-GIDG_A04 | Ensure sight glasses are clean and operational | 1 | D | 44 | 01 | 1010-P-001C 1D-44-01- | 1010-P-001C 1D-44-01- | OEC Tasks List
Gidgealpa Gas Satellite - Liquids Handling - Condensate Pump Package C | GIDG LIQ 1010-P-001C | 1010-P-001C | Pump-Condensate Duraqual PF1253-GIDG_A026 | Overhaul condensate pump high discharge pressure switch | 1 | Y | 01 | 00 |  |  | 2220763.docx
Gidgealpa Gas Satellite - Liquids Handling - Condensate Pump Package C | GIDG LIQ 1010-P-001C | 1010-P-001C | Pump-Condensate Duraqual PF1253-GIDG_A06 | Check gland packing on pumps and report if there is a fault | 1 | M | 44 | 01 | 1010-P-001C 1M-44-01- | 1010-P-001C 1M-44-01- | OEC Tasks List
Gidgealpa Gas Satellite - Liquids Handling - Condensate Pump Package C | GIDG LIQ 1010-P-001C | 1010-P-001C | Pump-Condensate Duraqual PF1253-GIDG_A09 | For Liquids Recovery Pump, Check for leaks | 1 | W | 44 | 01 | 1010-P-001C 1W-44-01- | 1010-P-001C 1W-44-01- | OEC Tasks List
Gidgealpa Gas Satellite - Liquids Handling - Condensate Pump Package C | GIDG LIQ 1010-P-001C | 1010-P-001C | Pump-Condensate Duraqual PF1253-GIDG_A033 | Ensure impulse lines are filled with the correct medium | 1 | Y | 01 | 00 |  |  | 2220763.docx
Gidgealpa Gas Satellite - Liquids Handling - Condensate Pump Package C | GIDG LIQ 1010-P-001C | 1010-P-001C | Pump-Condensate Duraqual PF1253-GIDG_A018 | Check pump foundation bolts are tight | 1 | Y | 4 | 00 |  |  | 2220246.docx
Gidgealpa Gas Satellite - Liquids Handling - Condensate Pump Package C | GIDG LIQ 1010-P-001C | 1010-P-001C | Pump-Condensate Duraqual PF1253-GIDG_A010 | For Liquids Recovery Pump, Check oil levels and top up as required | 1 | W | 44 | 01 | 1010-P-001C 1W-44-01- | 1010-P-001C 1W-44-01- | OEC Tasks List
Gidgealpa Gas Satellite - Liquids Handling - Condensate Pump Package C | GIDG LIQ 1010-P-001C | 1010-P-001C | Pump-Condensate Duraqual PF1253-GIDG_A01 | Ensure the condensate pumps are fully operational | 1 | W | 44 | 01 | 1010-P-001C 1W-44-01- | 1010-P-001C 1W-44-01- | OEC Tasks List
Gidgealpa Gas Satellite - Liquids Handling - Condensate Pump Package C | GIDG LIQ 1010-P-001C | 1010-P-001C | Pump-Condensate Duraqual PF1253-GIDG_A032 | Check tightness of impulse line supports | 1 | Y | 01 | 00 |  |  | 2220763.docx
Gidgealpa Gas Satellite - Liquids Handling - Condensate Pump Package C | GIDG LIQ 1010-P-001C | 1010-P-001C | Pump-Condensate Duraqual PF1253-GIDG_A015 | Check pulsation damper pre-charge pressure | 6 | M | 4 | 00 |  |  | 2218663.docx
Gidgealpa Gas Satellite - Liquids Handling - Condensate Pump Package C | GIDG LIQ 1010-P-001C | 1010-P-001C | Pump-Condensate Duraqual PF1253-GIDG_A017 | Check motor hold down bolts are tight | 1 | Y | 4 | 00 |  |  | 2220246.docx
Gidgealpa Gas Satellite - Liquids Handling - Condensate Pump Package C | GIDG LIQ 1010-P-001C | 1010-P-001C | Pump-Condensate Duraqual PF1253-GIDG_A027 | Inspect tube work for visible signs of wear | 1 | Y | 01 | 00 |  |  | 2220763.docx
Gidgealpa Gas Satellite - Liquids Handling - Condensate Pump Package C | GIDG LIQ 1010-P-001C | 1010-P-001C | Pump-Condensate Duraqual PF1253-GIDG_A02 | Check vessel and associated pipework for leaks | 1 | W | 44 | 01 | 1010-P-001C 1W-44-01- | 1010-P-001C 1W-44-01- | OEC Tasks List
Gidgealpa Gas Satellite - Liquids Handling - Condensate Pump Package C | GIDG LIQ 1010-P-001C | 1010-P-001C | Pump-Condensate Duraqual PF1253-GIDG_A019 | Clean pump crankcase oil leveller of sludge | 1 | Y | 4 | 00 |  |  | 2220246.docx
Gidgealpa Gas Satellite - Liquids Handling - Condensate Pump Package C | GIDG LIQ 1010-P-001C | 1010-P-001C | Pump-Condensate Duraqual PF1253-GIDG_A014 | Remove pump crankcase breather and clean with a non-explosive solvent | 6 | M | 4 | 00 |  |  | 2218663.docx | 001
Gidgealpa Gas Satellite - Liquids Handling - Condensate Pump Package C | GIDG LIQ 1010-P-001C | 1010-P-001C | Pump-Condensate Duraqual PF1253-GIDG_A020 | Ensure leveller is repositioned for correct crankcase oil level | 1 | Y | 4 | 00 |  |  | 2220246.docx
Gidgealpa Gas Satellite - Liquids Handling - Condensate Pump Package C | GIDG LIQ 1010-P-001C | 1010-P-001C | Pump-Condensate Duraqual PF1253-GIDG_A024 | Check pump pony rod for scoring | 1 | Y | 4 | 00 |  |  | 2220246.docx | 001
Gidgealpa Gas Satellite - Liquids Handling - Condensate Pump Package C | GIDG LIQ 1010-P-001C | 1010-P-001C | Pump-Condensate Duraqual PF1253-GIDG_A023 | Check pump plungers for scoring | 1 | Y | 4 | 00 |  |  | 2220246.docx
Gidgealpa Gas Satellite - Liquids Handling - Condensate Pump Package C | GIDG LIQ 1010-P-001C | 1010-P-001C | Pump-Condensate Duraqual PF1253-GIDG_A025 | Remove and replace NRV | 1 | Y | 4 | 00 |  |  | 2220246.docx | 001
Gidgealpa Gas Satellite - Liquids Handling - Condensate Pump Package C | GIDG LIQ 1010-P-001C | 1010-P-001C | Pump-Condensate Duraqual PF1253-GIDG_A012 | Clean sample point first, then run oil from the sample point to ensure the sample isn't contaminated | 6 | M | 4 | 00 |  |  | 2218663.docx | 001
Gidgealpa Gas Satellite - Liquids Handling - Condensate Pump Package C | GIDG LIQ 1010-P-001C | 1010-P-001C | Pump-Condensate Duraqual PF1253-GIDG_A013 | Replace pump lube oil filter using filter strap | 6 | M | 4 | 00 |  |  | 2218663.docx
Gidgealpa Gas Satellite - Liquids Handling - Condensate Pump Package C | GIDG LIQ 1010-P-001C | 1010-P-001C | Pump-Condensate Duraqual PF1253-GIDG_A011 | Take an oil sample | 6 | M | 4 | 00 |  |  | 2218663.docx
Gidgealpa Gas Satellite - Liquids Handling - Condensate Pump Package C | GIDG LIQ 1010-P-001C | 1010-P-001C | Pump-Condensate Duraqual PF1253-GIDG_A08 | Top up lubricator header | 1 | M | 44 | 01 | 1010-P-001C 1M-44-01- | 1010-P-001C 1M-44-01- | OEC Tasks List
Gidgealpa Gas Satellite - Liquids Handling - Condensate Pump Package C | GIDG LIQ 1010-P-001C | 1010-P-001C | Pump-Condensate Duraqual PF1253-GIDG_A07 | Top up crank case oil on all pumps | 1 | M | 44 | 01 | 1010-P-001C 1M-44-01- | 1010-P-001C 1M-44-01- | OEC Tasks List
Gidgealpa Gas Satellite - Liquids Handling - Condensate Pump Package C | GIDG LIQ 1010-EM-001C | 1010-EM-001C | Motor-Pump Toshiba-GIDG_A07 | Inspect gasket for deterioration and terminal box for contamination | 12 | M | 01 | 00 |  |  | 2219071.docx
Gidgealpa Gas Satellite - Liquids Handling - Condensate Pump Package C | GIDG LIQ 1010-EM-001C | 1010-EM-001C | Motor-Pump Toshiba-GIDG_A02 | Remove terminal box covers | 12 | M | 01 | 00 |  |  | 2219071.docx | 001
Gidgealpa Gas Satellite - Liquids Handling - Condensate Pump Package C | GIDG LIQ 1010-EM-001C | 1010-EM-001C | Motor-Pump Toshiba-GIDG_A04 | Check tightness of all local 3 phase and control terminations | 12 | M | 01 | 00 |  |  | 2219071.docx | 001
Gidgealpa Gas Satellite - Liquids Handling - Condensate Pump Package C | GIDG LIQ 1010-EM-001C | 1010-EM-001C | Motor-Pump Toshiba-GIDG_A03 | Inspect condition of 3 phase and control cables and lugs for deterioration, overheating and support in terminal box | 12 | M | 01 | 00 |  |  | 2219071.docx
Gidgealpa Gas Satellite - Liquids Handling - Condensate Pump Package C | GIDG LIQ 1010-EM-001C | 1010-EM-001C | Motor-Pump Toshiba-GIDG_A08 | Install terminal box covers | 12 | M | 01 | 00 |  |  | 2219071.docx
Gidgealpa Gas Satellite - Liquids Handling - Condensate Pump Package C | GIDG LIQ 1010-EM-001C | 1010-EM-001C | Motor-Pump Toshiba-GIDG_A01 | Inspect motor for excess dirt and oil build up in particular cooling fan inlet and outlet areas | 12 | M | 01 | 00 |  |  | 2219071.docx
Gidgealpa Gas Satellite - Liquids Handling - Condensate Pump Package C | GIDG LIQ 1010-EM-001C | 1010-EM-001C | Motor-Pump Toshiba-GIDG_A06 | Inspect condition of all earth wiring | 12 | M | 01 | 00 |  |  | 2219071.docx
Gidgealpa Gas Satellite - Liquids Handling - Condensate Pump Package C | GIDG LIQ 1010-EM-001C | 1010-EM-001C | Motor-Pump Toshiba-GIDG_A05 | Check tightness of earth wiring connections | 12 | M | 01 | 00 |  |  | 2219071.docx
Gidgealpa Gas Satellite - Liquids Handling - Condensate Pump Package C | GIDG LIQ 1010-EM-001C | 1010-EM-001C | Motor-Pump Toshiba-GIDG_A09 | Re-grease motor bearings | 12 | M | 01 | 00 |  |  | 2219071.docx
Gidgealpa Gas Satellite - Power Generation - LV Alternator Package A Unit 554 | GIDG PWR GEN 1010-G-001A | 1010-G-001A | Alternator-LV Caterpillar G3306-GIDG_A020 | Ensure terminals are tight and apply battery protector | 2 | M | 4 | 00 |  |  | 2231773.docx
Gidgealpa Gas Satellite - Power Generation - LV Alternator Package A Unit 554 | GIDG PWR GEN 1010-GX-001A | 1010-GX-001A | Alternator-LV Package IE Caterpillar G3306-GIDG_A076 | Lubricate Alternator Bearings | 1 | Y | 01 | 00 |  |  | 2219764.docx
Gidgealpa Gas Satellite - Power Generation - LV Alternator Package A Unit 554 | GIDG PWR GEN 1010-GX-001A | 1010-GX-001A | Alternator-LV Package IE Caterpillar G3306-GIDG_A061 | Inspect exterior of alternator unit for damage, missing bolts, missing or loose covers, missing cable ties, or a build up of oil or dust | 1 | Y | 01 | 00 |  |  | 2219764.docx
Gidgealpa Gas Satellite - Power Generation - LV Alternator Package A Unit 554 | GIDG PWR GEN 1010-GX-001A | 1010-GX-001A | Alternator-LV Package IE Caterpillar G3306-GIDG_A072 | Inspect all other terminals and circuit wiring connections on the Unit Control Panel for signs of heat discolouration | 1 | Y | 01 | 00 |  |  | 2219764.docx
Gidgealpa Gas Satellite - Power Generation - LV Alternator Package A Unit 554 | GIDG PWR GEN 1010-GX-001A | 1010-GX-001A | Alternator-LV Package IE Caterpillar G3306-GIDG_A074 | Inspect the Unit Control Panel door gasket for signs of dust ingress or gaskets damage | 1 | Y | 01 | 00 |  |  | 2219764.docx
Gidgealpa Gas Satellite - Power Generation - LV Alternator Package A Unit 554 | GIDG PWR GEN 1010-GX-001A | 1010-GX-001A | Alternator-LV Package IE Caterpillar G3306-GIDG_A067 | Inspect terminals and circuit wiring connections on the AVR unit for signs of heat discolouration | 1 | Y | 01 | 00 |  |  | 2219764.docx
Gidgealpa Gas Satellite - Power Generation - LV Alternator Package A Unit 554 | GIDG PWR GEN 1010-GX-001A | 1010-GX-001A | Alternator-LV Package IE Caterpillar G3306-GIDG_A066 | Inspect the condition of all panel meters | 1 | Y | 01 | 00 |  |  | 2219764.docx
Gidgealpa Gas Satellite - Power Generation - LV Alternator Package A Unit 554 | GIDG PWR GEN 1010-GX-001A | 1010-GX-001A | Alternator-LV Package IE Caterpillar G3306-GIDG_A071 | Check the AVR heat sink cooling fins for build up of dust, clean as required | 1 | Y | 01 | 00 |  |  | 2219764.docx
Gidgealpa Gas Satellite - Power Generation - LV Alternator Package A Unit 554 | GIDG PWR GEN 1010-GX-001A | 1010-GX-001A | Alternator-LV Package IE Caterpillar G3306-GIDG_A073 | Clean and vacuum the Unit Control Panel control cabinet, ensure all heat sink cooling fins are clean | 1 | Y | 01 | 00 |  |  | 2219764.docx
Gidgealpa Gas Satellite - Power Generation - LV Alternator Package A Unit 554 | GIDG PWR GEN 1010-GX-001A | 1010-GX-001A | Alternator-LV Package IE Caterpillar G3306-GIDG_A068 | Check the security of the connections by applying force to the wires | 1 | Y | 01 | 00 |  |  | 2219764.docx
Gidgealpa Gas Satellite - Power Generation - LV Alternator Package A Unit 554 | GIDG PWR GEN 1010-GX-001A | 1010-GX-001A | Alternator-LV Package IE Caterpillar G3306-GIDG_A077 | Clean off all expelled grease | 1 | Y | 01 | 00 |  |  | 2219764.docx
Gidgealpa Gas Satellite - Power Generation - LV Alternator Package A Unit 554 | GIDG PWR GEN 1010-GX-001A | 1010-GX-001A | Alternator-LV Package IE Caterpillar G3306-GIDG_A075 | Check the circuit breaker fixing bolts for tighness | 1 | Y | 01 | 00 |  |  | 2219764.docx
Gidgealpa Gas Satellite - Power Generation - LV Alternator Package A Unit 554 | GIDG PWR GEN 1010-GX-001A | 1010-GX-001A | Alternator-LV Package IE Caterpillar G3306-GIDG_A080 | Check battery electrolyte level in each cell, top up if required with de-min water | 1 | Y | 01 | 00 |  |  | 2219764.docx
Gidgealpa Gas Satellite - Power Generation - LV Alternator Package A Unit 554 | GIDG PWR GEN 1010-GX-001A | 1010-GX-001A | Alternator-LV Package IE Caterpillar G3306-GIDG_A078 | Inspect power cabling from the Alternator to the circuit breaker | 1 | Y | 01 | 00 |  |  | 2219764.docx
Gidgealpa Gas Satellite - Power Generation - LV Alternator Package A Unit 554 | GIDG PWR GEN 1010-GX-001A | 1010-GX-001A | Alternator-LV Package IE Caterpillar G3306-GIDG_A081 | Check battery terminals for corrosion | 1 | Y | 01 | 00 |  |  | 2219764.docx
Gidgealpa Gas Satellite - Power Generation - LV Alternator Package A Unit 554 | GIDG PWR GEN 1010-GX-001A | 1010-GX-001A | Alternator-LV Package IE Caterpillar G3306-GIDG_A069 | Inspect exterior condition of AVR for damaged panels or missing screws | 1 | Y | 01 | 00 |  |  | 2219764.docx
Gidgealpa Gas Satellite - Power Generation - LV Alternator Package A Unit 554 | GIDG PWR GEN 1010-GX-001A | 1010-GX-001A | Alternator-LV Package IE Caterpillar G3306-GIDG_A060 | Check Electrical Hazard Warning signs to ensure they are securely mounted and legible | 1 | Y | 01 | 00 |  |  | 2219764.docx
Gidgealpa Gas Satellite - Power Generation - LV Alternator Package A Unit 554 | GIDG PWR GEN 1010-GX-001A | 1010-GX-001A | Alternator-LV Package IE Caterpillar G3306-GIDG_A065 | Inspect condition of all Unit Control Panel buttons for damage that prevents normal operation | 1 | Y | 01 | 00 |  |  | 2219764.docx
Gidgealpa Gas Satellite - Power Generation - LV Alternator Package A Unit 554 | GIDG PWR GEN 1010-GX-001A | 1010-GX-001A | Alternator-LV Package IE Caterpillar G3306-GIDG_A064 | Inspect all Alternator External Earth connections for signs of corrosion and check earth cable connections for tightness | 1 | Y | 01 | 00 |  |  | 2219764.docx
Gidgealpa Gas Satellite - Power Generation - LV Alternator Package A Unit 554 | GIDG PWR GEN 1010-GX-001A | 1010-GX-001A | Alternator-LV Package IE Caterpillar G3306-GIDG_A079 | Inspect power cabling for loose or missing supports, missing cable ties or contact with sharp edges / rough surfaces | 1 | Y | 01 | 00 |  |  | 2219764.docx
Gidgealpa Gas Satellite - Power Generation - LV Alternator Package A Unit 554 | GIDG PWR GEN 1010-GX-001A | 1010-GX-001A | Alternator-LV Package IE Caterpillar G3306-GIDG_A059 | Ensure all redundant items not required in the electrical panels | 1 | Y | 01 | 00 |  |  | 2219764.docx
Gidgealpa Gas Satellite - Power Generation - LV Alternator Package A Unit 554 | GIDG PWR GEN 1010-GX-001A | 1010-GX-001A | Alternator-LV Package IE Caterpillar G3306-GIDG_A070 | Inspect all electronic components and potentiometers on the AVR for signs of heat discolouration | 1 | Y | 01 | 00 |  |  | 2219764.docx
Gidgealpa Gas Satellite - Power Generation - LV Alternator Package A Unit 554 | GIDG PWR GEN 1010-GX-001A | 1010-GX-001A | Alternator-LV Package IE Caterpillar G3306-GIDG_A062 | Inspect external Earth connections at Alternator Main Terminal Box for signs of corrosion and check earth cable connections for tightness | 1 | Y | 01 | 00 |  |  | 2219764.docx
Gidgealpa Gas Satellite - Power Generation - LV Alternator Package A Unit 554 | GIDG PWR GEN 1010-GX-001A | 1010-GX-001A | Alternator-LV Package IE Caterpillar G3306-GIDG_A063 | Clean off any corrosion and repair, re-terminate or tighten connection if required | 1 | Y | 01 | 00 |  |  | 2219764.docx
Gidgealpa Gas Satellite - Power Generation - LV Alternator Package A Unit 554 | GIDG PWR GEN 1010-GX-001A | 1010-GX-001A | Alternator-LV Package IE Caterpillar G3306-GIDG_A082 | Check the battery charger amp meter, float voltage and boost voltage for expected values | 1 | Y | 01 | 00 |  |  | 2219764.docx
Gidgealpa Gas Satellite - Power Generation - LV Alternator Package A Unit 554 | GIDG PWR GEN 1010-GX-001A | 1010-GX-001A | Alternator-LV Package IE Caterpillar G3306-GIDG_A083 | Inspect the condition of all charger panel meters and ensure they operate as expected | 1 | Y | 01 | 00 |  |  | 2219764.docx
Gidgealpa Gas Satellite - Power Generation - LV Alternator Package A Unit 554 | GIDG PWR GEN 1010-GE-001A | 1010-GE-001A | Alternator-LV Caterpillar G3306-GIDG_A032 | Inspect air intake hoses for deterioration or cracks | 6 | M | 4 | 00 |  |  | 2232159.docx
Gidgealpa Gas Satellite - Power Generation - LV Alternator Package A Unit 554 | GIDG PWR GEN 1010-GE-001A | 1010-GE-001A | Alternator-LV Caterpillar G3306-GIDG_A033 | Inspect all coolant hoses and pipe joints for leaks | 6 | M | 4 | 00 |  |  | 2232159.docx
Gidgealpa Gas Satellite - Power Generation - LV Alternator Package A Unit 554 | GIDG PWR GEN 1010-GE-001A | 1010-GE-001A | Alternator-LV Caterpillar G3306-GIDG_A034 | Ensure hoses are in good condition | 6 | M | 4 | 00 |  |  | 2232159.docx
Gidgealpa Gas Satellite - Power Generation - LV Alternator Package A Unit 554 | GIDG PWR GEN 1010-GE-001A | 1010-GE-001A | Alternator-LV Caterpillar G3306-GIDG_A026 | Clean and remove any blockages | 2 | M | 4 | 00 |  |  | 2231773.docx
Gidgealpa Gas Satellite - Power Generation - LV Alternator Package A Unit 554 | GIDG PWR GEN 1010-GE-001A | 1010-GE-001A | Alternator-LV Caterpillar G3306-GIDG_A025 | Check radiator cores for blockage | 2 | M | 4 | 00 |  |  | 2231773.docx
Gidgealpa Gas Satellite - Power Generation - LV Alternator Package A Unit 554 | GIDG PWR GEN 1010-GE-001A | 1010-GE-001A | Alternator-LV Caterpillar G3306-GIDG_A051 | Remove and clean engine oil auto leveller | 1 | Y | 4 | 00 |  |  | 2232756.docx
Gidgealpa Gas Satellite - Power Generation - LV Alternator Package A Unit 554 | GIDG PWR GEN 1010-GE-001A | 1010-GE-001A | Alternator-LV Caterpillar G3306-GIDG_A043 | Remove and replace the engine oil filter | 1 | Y | 4 | 00 |  |  | 2232756.docx
Gidgealpa Gas Satellite - Power Generation - LV Alternator Package A Unit 554 | GIDG PWR GEN 1010-GE-001A | 1010-GE-001A | Alternator-LV Caterpillar G3306-GIDG_A044 | Replace the engine drain plugs | 1 | Y | 4 | 00 |  |  | 2232756.docx
Gidgealpa Gas Satellite - Power Generation - LV Alternator Package A Unit 554 | GIDG PWR GEN 1010-GE-001A | 1010-GE-001A | Alternator-LV Caterpillar G3306-GIDG_A042 | Drain the oil from the engine | 1 | Y | 4 | 00 |  |  | 2232756.docx
Gidgealpa Gas Satellite - Power Generation - LV Alternator Package A Unit 554 | GIDG PWR GEN 1010-GE-001A | 1010-GE-001A | Alternator-LV Caterpillar G3306-GIDG_A02 | Check cooling system for leaks, check level and top up as required | 1 | W | 44 | 01 | 1010-GE-001A 1W-44-01- | 1010-GE-001A 1W-44-01- | OEC Tasks List
Gidgealpa Gas Satellite - Power Generation - LV Alternator Package A Unit 554 | GIDG PWR GEN 1010-GE-001A | 1010-GE-001A | Alternator-LV Caterpillar G3306-GIDG_A01 | Check engine oil levels, check for leaks | 1 | W | 44 | 01 | 1010-GE-001A 1W-44-01- | 1010-GE-001A 1W-44-01- | OEC Tasks List
Gidgealpa Gas Satellite - Power Generation - LV Alternator Package A Unit 554 | GIDG PWR GEN 1010-GE-001A | 1010-GE-001A | Alternator-LV Caterpillar G3306-GIDG_A045 | Fill the engine with oil | 1 | Y | 4 | 00 |  |  | 2232756.docx
Gidgealpa Gas Satellite - Power Generation - LV Alternator Package A Unit 554 | GIDG PWR GEN 1010-GE-001A | 1010-GE-001A | Alternator-LV Caterpillar G3306-GIDG_A019 | Check terminal and connector for corrosion and condition | 2 | M | 4 | 00 |  |  | 2231773.docx
Gidgealpa Gas Satellite - Power Generation - LV Alternator Package A Unit 554 | GIDG PWR GEN 1010-GE-001A | 1010-GE-001A | Alternator-LV Caterpillar G3306-GIDG_A018 | Clean positive and negative battery terminals and cable connectors with wire brush | 2 | M | 4 | 00 |  |  | 2231773.docx
Gidgealpa Gas Satellite - Power Generation - LV Alternator Package A Unit 554 | GIDG PWR GEN 1010-GE-001A | 1010-GE-001A | Alternator-LV Caterpillar G3306-GIDG_A020 | Ensure terminals are tight and apply battery protector | 2 | M | 4 | 00 |  |  | 2231773.docx
Gidgealpa Gas Satellite - Power Generation - LV Alternator Package A Unit 554 | GIDG PWR GEN 1010-GE-001A | 1010-GE-001A | Alternator-LV Caterpillar G3306-GIDG_A037 | Check wiring continuity and resistance in activated and non-activated state | 6 | M | 4 | 00 |  |  | 2232159.docx
Gidgealpa Gas Satellite - Power Generation - LV Alternator Package A Unit 554 | GIDG PWR GEN 1010-GE-001A | 1010-GE-001A | Alternator-LV Caterpillar G3306-GIDG_A035 | Check all exposed wiring for chaffing | 6 | M | 4 | 00 |  |  | 2232159.docx
Gidgealpa Gas Satellite - Power Generation - LV Alternator Package A Unit 554 | GIDG PWR GEN 1010-GE-001A | 1010-GE-001A | Alternator-LV Caterpillar G3306-GIDG_A017 | Remove battery cables at battery | 2 | M | 4 | 00 |  |  | 2231773.docx
Gidgealpa Gas Satellite - Power Generation - LV Alternator Package A Unit 554 | GIDG PWR GEN 1010-GE-001A | 1010-GE-001A | Alternator-LV Caterpillar G3306-GIDG_A041 | Inspect wiring | 6 | M | 4 | 00 |  |  | 2232574.docx
Gidgealpa Gas Satellite - Power Generation - LV Alternator Package A Unit 554 | GIDG PWR GEN 1010-GE-001A | 1010-GE-001A | Alternator-LV Caterpillar G3306-GIDG_A010 | Replace oil filter | 2 | M | 4 | 00 |  |  | 2231773.docx
Gidgealpa Gas Satellite - Power Generation - LV Alternator Package A Unit 554 | GIDG PWR GEN 1010-GE-001A | 1010-GE-001A | Alternator-LV Caterpillar G3306-GIDG_A055 | Re-dose coolant if required | 1 | Y | 4 | 00 |  |  | 2232756.docx
Gidgealpa Gas Satellite - Power Generation - LV Alternator Package A Unit 554 | GIDG PWR GEN 1010-GE-001A | 1010-GE-001A | Alternator-LV Caterpillar G3306-GIDG_A07 | Change oil using drain valves | 2 | M | 4 | 00 |  |  | 2231773.docx
Gidgealpa Gas Satellite - Power Generation - LV Alternator Package A Unit 554 | GIDG PWR GEN 1010-GE-001A | 1010-GE-001A | Alternator-LV Caterpillar G3306-GIDG_A012 | Inspect filter condition and clean or replace as required | 2 | M | 4 | 00 |  |  | 2231773.docx
Gidgealpa Gas Satellite - Power Generation - LV Alternator Package A Unit 554 | GIDG PWR GEN 1010-GE-001A | 1010-GE-001A | Alternator-LV Caterpillar G3306-GIDG_A027 | Adjust valve lash / tappets | 2 | M | 4 | 00 |  |  | 2231773.docx
Gidgealpa Gas Satellite - Power Generation - LV Alternator Package A Unit 554 | GIDG PWR GEN 1010-GE-001A | 1010-GE-001A | Alternator-LV Caterpillar G3306-GIDG_A03 | Check air filter blockage indicators, air cooling system water flow | 1 | W | 44 | 01 | 1010-GE-001A 1W-44-01- | 1010-GE-001A 1W-44-01- | OEC Tasks List
Gidgealpa Gas Satellite - Power Generation - LV Alternator Package A Unit 554 | GIDG PWR GEN 1010-GE-001A | 1010-GE-001A | Alternator-LV Caterpillar G3306-GIDG_A053 | Clean and remove any corrosion buildup | 1 | Y | 4 | 00 |  |  | 2232756.docx
Gidgealpa Gas Satellite - Power Generation - LV Alternator Package A Unit 554 | GIDG PWR GEN 1010-GE-001A | 1010-GE-001A | Alternator-LV Caterpillar G3306-GIDG_A052 | Remove leads from coils & check for corrosion | 1 | Y | 4 | 00 |  |  | 2232756.docx
Gidgealpa Gas Satellite - Power Generation - LV Alternator Package A Unit 554 | GIDG PWR GEN 1010-GE-001A | 1010-GE-001A | Alternator-LV Caterpillar G3306-GIDG_A011 | Re-fill sump with new oil to correct level | 2 | M | 4 | 00 |  |  | 2231773.docx
Gidgealpa Gas Satellite - Power Generation - LV Alternator Package A Unit 554 | GIDG PWR GEN 1010-GE-001A | 1010-GE-001A | Alternator-LV Caterpillar G3306-GIDG_A048 | Clean filter housing | 1 | Y | 4 | 00 |  |  | 2232756.docx
Gidgealpa Gas Satellite - Power Generation - LV Alternator Package A Unit 554 | GIDG PWR GEN 1010-GE-001A | 1010-GE-001A | Alternator-LV Caterpillar G3306-GIDG_A08 | Re-fit plugs and close drain line valves | 2 | M | 4 | 00 |  |  | 2231773.docx
Gidgealpa Gas Satellite - Power Generation - LV Alternator Package A Unit 554 | GIDG PWR GEN 1010-GE-001A | 1010-GE-001A | Alternator-LV Caterpillar G3306-GIDG_A049 | Replace spark plugs | 1 | Y | 4 | 00 |  |  | 2232756.docx
Gidgealpa Gas Satellite - Power Generation - LV Alternator Package A Unit 554 | GIDG PWR GEN 1010-GE-001A | 1010-GE-001A | Alternator-LV Caterpillar G3306-GIDG_A054 | Test coolant using Nalco kit | 1 | Y | 4 | 00 |  |  | 2232756.docx
Gidgealpa Gas Satellite - Power Generation - LV Alternator Package A Unit 554 | GIDG PWR GEN 1010-GE-001A | 1010-GE-001A | Alternator-LV Caterpillar G3306-GIDG_A050 | Replace radiator cap | 1 | Y | 4 | 00 |  |  | 2232756.docx
Gidgealpa Gas Satellite - Power Generation - LV Alternator Package A Unit 554 | GIDG PWR GEN 1010-GE-001A | 1010-GE-001A | Alternator-LV Caterpillar G3306-GIDG_A09 | Take oil sample | 2 | M | 4 | 00 |  |  | 2231773.docx
Gidgealpa Gas Satellite - Power Generation - LV Alternator Package A Unit 554 | GIDG PWR GEN 1010-GE-001A | 1010-GE-001A | Alternator-LV Caterpillar G3306-GIDG_A058 | Carry Out Top End Overhaul | 3 | Y | 4 | 00 |  |  | 2256646.docx
Gidgealpa Gas Satellite - Power Generation - LV Alternator Package A Unit 554 | GIDG PWR GEN 1010-GE-001A | 1010-GE-001A | Alternator-LV Caterpillar G3306-GIDG_A013 | Clean filter and housing | 2 | M | 4 | 00 |  |  | 2231773.docx
Gidgealpa Gas Satellite - Power Generation - LV Alternator Package A Unit 554 | GIDG PWR GEN 1010-GE-001A | 1010-GE-001A | Alternator-LV Caterpillar G3306-GIDG_A057 | Carry out Unit Overhaul | 3 | Y | 4 | 00 |  |  | 2222484.docx
Gidgealpa Gas Satellite - Power Generation - LV Alternator Package A Unit 554 | GIDG PWR GEN 1010-GE-001A | 1010-GE-001A | Alternator-LV Caterpillar G3306-GIDG_A024 | Check coolant level | 2 | M | 4 | 00 |  |  | 2231773.docx
Gidgealpa Gas Satellite - Power Generation - LV Alternator Package A Unit 554 | GIDG PWR GEN 1010-GE-001A | 1010-GE-001A | Alternator-LV Caterpillar G3306-GIDG_A016 | Check the electrolyte level in the batteries and top up as required | 2 | M | 4 | 00 |  |  | 2231773.docx
Gidgealpa Gas Satellite - Power Generation - LV Alternator Package A Unit 554 | GIDG PWR GEN 1010-GE-001A | 1010-GE-001A | Alternator-LV Caterpillar G3306-GIDG_A023 | Replace fan belt or alternator belt | 2 | M | 4 | 00 |  |  | 2231773.docx | 001
Gidgealpa Gas Satellite - Power Generation - LV Alternator Package A Unit 554 | GIDG PWR GEN 1010-GE-001A | 1010-GE-001A | Alternator-LV Caterpillar G3306-GIDG_A022 | Check fan belt condition | 2 | M | 4 | 00 |  |  | 2231773.docx | 001
Gidgealpa Gas Satellite - Power Generation - LV Alternator Package A Unit 554 | GIDG PWR GEN 1010-GE-001A | 1010-GE-001A | Alternator-LV Caterpillar G3306-GIDG_A030 | Clean crankcase breather | 2 | M | 4 | 00 |  |  | 2231773.docx
Gidgealpa Gas Satellite - Power Generation - LV Alternator Package A Unit 554 | GIDG PWR GEN 1010-GE-001A | 1010-GE-001A | Alternator-LV Caterpillar G3306-GIDG_A014 | Replace air filter element and clean housing | 2 | M | 4 | 00 |  |  | 2231773.docx
Gidgealpa Gas Satellite - Power Generation - LV Alternator Package A Unit 554 | GIDG PWR GEN 1010-GE-001A | 1010-GE-001A | Alternator-LV Caterpillar G3306-GIDG_A028 | Check and adjust intake and exhaust valve lash | 2 | M | 4 | 00 |  |  | 2231773.docx
Gidgealpa Gas Satellite - Power Generation - LV Alternator Package A Unit 554 | GIDG PWR GEN 1010-GE-001A | 1010-GE-001A | Alternator-LV Caterpillar G3306-GIDG_A040 | Ensure alignment of drive has not altered If replacements or re-tensioning | 6 | M | 4 | 00 |  |  | 2232574.docx
Gidgealpa Gas Satellite - Power Generation - LV Alternator Package A Unit 554 | GIDG PWR GEN 1010-GE-001A | 1010-GE-001A | Alternator-LV Caterpillar G3306-GIDG_A031 | Lubricate carburettor linkage | 2 | M | 4 | 00 |  |  | 2231773.docx
Gidgealpa Gas Satellite - Power Generation - LV Alternator Package A Unit 554 | GIDG PWR GEN 1010-GE-001A | 1010-GE-001A | Alternator-LV Caterpillar G3306-GIDG_A015 | Clean oil header tank sight glasses & breather | 2 | M | 4 | 00 |  |  | 2231773.docx
Gidgealpa Gas Satellite - Power Generation - LV Alternator Package A Unit 554 | GIDG PWR GEN 1010-GE-001A | 1010-GE-001A | Alternator-LV Caterpillar G3306-GIDG_A029 | Re-fit existing rocker cover gasket and tension rocker cover | 2 | M | 4 | 00 |  |  | 2231773.docx
Gidgealpa Gas Satellite - Power Generation - LV Alternator Package A Unit 554 | GIDG PWR GEN 1010-GE-001A | 1010-GE-001A | Alternator-LV Caterpillar G3306-GIDG_A047 | Replace air filter element | 1 | Y | 4 | 00 |  |  | 2232756.docx
Gidgealpa Gas Satellite - Power Generation - LV Alternator Package A Unit 554 | GIDG PWR GEN 1010-GE-001A | 1010-GE-001A | Alternator-LV Caterpillar G3306-GIDG_A021 | Lubricate fan drive & Idler pulley | 2 | M | 4 | 00 |  |  | 2231773.docx
Gidgealpa Gas Satellite - Power Generation - LV Alternator Package A Unit 554 | GIDG PWR GEN 1010-GE-001A | 1010-GE-001A | Alternator-LV Caterpillar G3306-GIDG_A038 | Lubricate rear alternator bearing | 6 | M | 4 | 00 |  |  | 2232159.docx
Gidgealpa Gas Satellite - Power Generation - LV Alternator Package A Unit 554 | GIDG PWR GEN 1010-GE-001A | 1010-GE-001A | Alternator-LV Caterpillar G3306-GIDG_A06 | For Emergency Diesel Generator, Check diesel Fuel level | 1 | W | 44 | 01 | 1010-GE-001A 1W-44-01- | 1010-GE-001A 1W-44-01- | OEC Tasks List
Gidgealpa Gas Satellite - Power Generation - LV Alternator Package A Unit 554 | GIDG PWR GEN 1010-GE-001A | 1010-GE-001A | Alternator-LV Caterpillar G3306-GIDG_A046 | Inspect the engine fill and drain points for visible oil leaks, clean and repair as required | 1 | Y | 4 | 00 |  |  | 2232756.docx
Gidgealpa Gas Satellite - Power Generation - LV Alternator Package A Unit 554 | GIDG PWR GEN 1010-GE-001A | 1010-GE-001A | Alternator-LV Caterpillar G3306-GIDG_A05 | For Emergency Diesel Generator, Start the set and run to check running condition | 1 | W | 44 | 01 | 1010-GE-001A 1W-44-01- | 1010-GE-001A 1W-44-01- | OEC Tasks List
Gidgealpa Gas Satellite - Power Generation - LV Alternator Package A Unit 554 | GIDG PWR GEN 1010-GE-001A | 1010-GE-001A | Alternator-LV Caterpillar G3306-GIDG_A04 | Check for abnormal noise from engine | 1 | W | 44 | 01 | 1010-GE-001A 1W-44-01-001 | 1010-GE-001A 1W-44-01-001 | OEC Tasks List | 001
Gidgealpa Gas Satellite - Power Generation - LV Alternator Package A Unit 554 | GIDG PWR GEN 1010-GE-001A | 1010-GE-001A | Alternator-LV Caterpillar G3306-GIDG_A039 | Inspect engine mounts for cracks or looseness | 6 | M | 4 | 00 |  |  | 2232574.docx
Gidgealpa Gas Satellite - Power Generation - LV Alternator Package A Unit 554 | GIDG PWR GEN 1010-GE-001A | 1010-GE-001A | Alternator-LV Caterpillar G3306-GIDG_A036 | Function test oil press low shutdown switch | 6 | M | 4 | 00 |  |  | 2232159.docx
Gidgealpa Gas Satellite - Power Generation - LV Alternator Package A Unit 554 | GIDG PWR GEN 1010-GE-001A | 1010-GE-001A | Alternator-LV Caterpillar G3306-GIDG_A056 | Replace cylinder head temp shutdown switch | 1 | Y | 01 | 00 |  |  | 2232756.docx
Gidgealpa Gas Satellite - Power Generation - LV Alternator Package A Unit 554 | GIDG PWR GEN 1010-G-001A | 1010-G-001A | Alternator-LV Caterpillar G3306-GIDG_A025 | Check radiator cores for blockage | 2 | M | 4 | 00 |  |  | 2231773.docx
Gidgealpa Gas Satellite - Power Generation - LV Alternator Package A Unit 554 | GIDG PWR GEN 1010-G-001A | 1010-G-001A | Alternator-LV Caterpillar G3306-GIDG_A033 | Inspect all coolant hoses and pipe joints for leaks | 6 | M | 4 | 00 |  |  | 2232159.docx
Gidgealpa Gas Satellite - Power Generation - LV Alternator Package A Unit 554 | GIDG PWR GEN 1010-G-001A | 1010-G-001A | Alternator-LV Caterpillar G3306-GIDG_A026 | Clean and remove any blockages | 2 | M | 4 | 00 |  |  | 2231773.docx
Gidgealpa Gas Satellite - Power Generation - LV Alternator Package A Unit 554 | GIDG PWR GEN 1010-G-001A | 1010-G-001A | Alternator-LV Caterpillar G3306-GIDG_A034 | Ensure hoses are in good condition | 6 | M | 4 | 00 |  |  | 2232159.docx
Gidgealpa Gas Satellite - Power Generation - LV Alternator Package A Unit 554 | GIDG PWR GEN 1010-G-001A | 1010-G-001A | Alternator-LV Caterpillar G3306-GIDG_A032 | Inspect air intake hoses for deterioration or cracks | 6 | M | 4 | 00 |  |  | 2232159.docx
Gidgealpa Gas Satellite - Power Generation - LV Alternator Package A Unit 554 | GIDG PWR GEN 1010-G-001A | 1010-G-001A | Alternator-LV Caterpillar G3306-GIDG_A038 | Lubricate rear alternator bearing | 6 | M | 4 | 00 |  |  | 2232159.docx
Gidgealpa Gas Satellite - Power Generation - LV Alternator Package A Unit 554 | GIDG PWR GEN 1010-G-001A | 1010-G-001A | Alternator-LV Caterpillar G3306-GIDG_A036 | Function test oil press low shutdown switch | 6 | M | 4 | 00 |  |  | 2232159.docx
Gidgealpa Gas Satellite - Power Generation - LV Alternator Package A Unit 554 | GIDG PWR GEN 1010-G-001A | 1010-G-001A | Alternator-LV Caterpillar G3306-GIDG_A056 | Replace cylinder head temp shutdown switch | 1 | Y | 01 | 00 |  |  | 2232756.docx
Gidgealpa Gas Satellite - Power Generation - LV Alternator Package A Unit 554 | GIDG PWR GEN 1010-G-001A | 1010-G-001A | Alternator-LV Caterpillar G3306-GIDG_A04 | Check for abnormal noise from engine | 1 | W | 44 | 01 | 1010-G-001A 1W-44-01- | 1010-G-001A 1W-44-01- | OEC Tasks List
Gidgealpa Gas Satellite - Power Generation - LV Alternator Package A Unit 554 | GIDG PWR GEN 1010-G-001A | 1010-G-001A | Alternator-LV Caterpillar G3306-GIDG_A046 | Inspect the engine fill and drain points for visible oil leaks, clean and repair as required | 1 | Y | 4 | 00 |  |  | 2232756.docx
Gidgealpa Gas Satellite - Power Generation - LV Alternator Package A Unit 554 | GIDG PWR GEN 1010-G-001A | 1010-G-001A | Alternator-LV Caterpillar G3306-GIDG_A06 | For Emergency Diesel Generator, Check diesel Fuel level | 1 | W | 44 | 01 | 1010-G-001A 1W-44-01- | 1010-G-001A 1W-44-01- | OEC Tasks List
Gidgealpa Gas Satellite - Power Generation - LV Alternator Package A Unit 554 | GIDG PWR GEN 1010-G-001A | 1010-G-001A | Alternator-LV Caterpillar G3306-GIDG_A039 | Inspect engine mounts for cracks or looseness | 6 | M | 4 | 00 |  |  | 2232574.docx
Gidgealpa Gas Satellite - Power Generation - LV Alternator Package A Unit 554 | GIDG PWR GEN 1010-G-001A | 1010-G-001A | Alternator-LV Caterpillar G3306-GIDG_A05 | For Emergency Diesel Generator, Start the set and run to check running condition | 1 | W | 44 | 01 | 1010-G-001A 1W-44-01- | 1010-G-001A 1W-44-01- | OEC Tasks List
Gidgealpa Gas Satellite - Power Generation - LV Alternator Package A Unit 554 | GIDG PWR GEN 1010-G-001A | 1010-G-001A | Alternator-LV Caterpillar G3306-GIDG_A02 | Check cooling system for leaks, check level and top up as required | 1 | W | 44 | 01 | 1010-G-001A 1W-44-01- | 1010-G-001A 1W-44-01- | OEC Tasks List
Gidgealpa Gas Satellite - Power Generation - LV Alternator Package A Unit 554 | GIDG PWR GEN 1010-G-001A | 1010-G-001A | Alternator-LV Caterpillar G3306-GIDG_A042 | Drain the oil from the engine | 1 | Y | 4 | 00 |  |  | 2232756.docx
Gidgealpa Gas Satellite - Power Generation - LV Alternator Package A Unit 554 | GIDG PWR GEN 1010-G-001A | 1010-G-001A | Alternator-LV Caterpillar G3306-GIDG_A043 | Remove and replace the engine oil filter | 1 | Y | 4 | 00 |  |  | 2232756.docx
Gidgealpa Gas Satellite - Power Generation - LV Alternator Package A Unit 554 | GIDG PWR GEN 1010-G-001A | 1010-G-001A | Alternator-LV Caterpillar G3306-GIDG_A045 | Fill the engine with oil | 1 | Y | 4 | 00 |  |  | 2232756.docx
Gidgealpa Gas Satellite - Power Generation - LV Alternator Package A Unit 554 | GIDG PWR GEN 1010-G-001A | 1010-G-001A | Alternator-LV Caterpillar G3306-GIDG_A044 | Replace the engine drain plugs | 1 | Y | 4 | 00 |  |  | 2232756.docx
Gidgealpa Gas Satellite - Power Generation - LV Alternator Package A Unit 554 | GIDG PWR GEN 1010-G-001A | 1010-G-001A | Alternator-LV Caterpillar G3306-GIDG_A051 | Remove and clean engine oil auto leveller | 1 | Y | 4 | 00 |  |  | 2232756.docx
Gidgealpa Gas Satellite - Power Generation - LV Alternator Package A Unit 554 | GIDG PWR GEN 1010-G-001A | 1010-G-001A | Alternator-LV Caterpillar G3306-GIDG_A01 | Check engine oil levels, check for leaks | 1 | W | 44 | 01 | 1010-G-001A 1W-44-01- | 1010-G-001A 1W-44-01- | OEC Tasks List
Gidgealpa Gas Satellite - Power Generation - LV Alternator Package A Unit 554 | GIDG PWR GEN 1010-G-001A | 1010-G-001A | Alternator-LV Caterpillar G3306-GIDG_A03 | Check air filter blockage indicators, air cooling system water flow | 1 | W | 44 | 01 | 1010-G-001A 1W-44-01- | 1010-G-001A 1W-44-01- | OEC Tasks List
Gidgealpa Gas Satellite - Power Generation - LV Alternator Package A Unit 554 | GIDG PWR GEN 1010-G-001A | 1010-G-001A | Alternator-LV Caterpillar G3306-GIDG_A024 | Check coolant level | 2 | M | 4 | 00 |  |  | 2231773.docx
Gidgealpa Gas Satellite - Power Generation - LV Alternator Package A Unit 554 | GIDG PWR GEN 1010-G-001A | 1010-G-001A | Alternator-LV Caterpillar G3306-GIDG_A027 | Adjust valve lash / tappets | 2 | M | 4 | 00 |  |  | 2231773.docx
Gidgealpa Gas Satellite - Power Generation - LV Alternator Package A Unit 554 | GIDG PWR GEN 1010-G-001A | 1010-G-001A | Alternator-LV Caterpillar G3306-GIDG_A053 | Clean and remove any corrosion buildup | 1 | Y | 4 | 00 |  |  | 2232756.docx | 001
Gidgealpa Gas Satellite - Power Generation - LV Alternator Package A Unit 554 | GIDG PWR GEN 1010-G-001A | 1010-G-001A | Alternator-LV Caterpillar G3306-GIDG_A023 | Replace fan belt or alternator belt | 2 | M | 4 | 00 |  |  | 2231773.docx
Gidgealpa Gas Satellite - Power Generation - LV Alternator Package A Unit 554 | GIDG PWR GEN 1010-G-001A | 1010-G-001A | Alternator-LV Caterpillar G3306-GIDG_A014 | Replace air filter element and clean housing | 2 | M | 4 | 00 |  |  | 2231773.docx | 001
Gidgealpa Gas Satellite - Power Generation - LV Alternator Package A Unit 554 | GIDG PWR GEN 1010-G-001A | 1010-G-001A | Alternator-LV Caterpillar G3306-GIDG_A030 | Clean crankcase breather | 2 | M | 4 | 00 |  |  | 2231773.docx | 001
Gidgealpa Gas Satellite - Power Generation - LV Alternator Package A Unit 554 | GIDG PWR GEN 1010-G-001A | 1010-G-001A | Alternator-LV Caterpillar G3306-GIDG_A016 | Check the electrolyte level in the batteries and top up as required | 2 | M | 4 | 00 |  |  | 2231773.docx
Gidgealpa Gas Satellite - Power Generation - LV Alternator Package A Unit 554 | GIDG PWR GEN 1010-G-001A | 1010-G-001A | Alternator-LV Caterpillar G3306-GIDG_A040 | Ensure alignment of drive has not altered If replacements or re-tensioning | 6 | M | 4 | 00 |  |  | 2232574.docx
Gidgealpa Gas Satellite - Power Generation - LV Alternator Package A Unit 554 | GIDG PWR GEN 1010-G-001A | 1010-G-001A | Alternator-LV Caterpillar G3306-GIDG_A047 | Replace air filter element | 1 | Y | 4 | 00 |  |  | 2232756.docx
Gidgealpa Gas Satellite - Power Generation - LV Alternator Package A Unit 554 | GIDG PWR GEN 1010-G-001A | 1010-G-001A | Alternator-LV Caterpillar G3306-GIDG_A031 | Lubricate carburettor linkage | 2 | M | 4 | 00 |  |  | 2231773.docx
Gidgealpa Gas Satellite - Power Generation - LV Alternator Package A Unit 554 | GIDG PWR GEN 1010-G-001A | 1010-G-001A | Alternator-LV Caterpillar G3306-GIDG_A028 | Check and adjust intake and exhaust valve lash | 2 | M | 4 | 00 |  |  | 2231773.docx
Gidgealpa Gas Satellite - Power Generation - LV Alternator Package A Unit 554 | GIDG PWR GEN 1010-G-001A | 1010-G-001A | Alternator-LV Caterpillar G3306-GIDG_A029 | Re-fit existing rocker cover gasket and tension rocker cover | 2 | M | 4 | 00 |  |  | 2231773.docx
Gidgealpa Gas Satellite - Power Generation - LV Alternator Package A Unit 554 | GIDG PWR GEN 1010-G-001A | 1010-G-001A | Alternator-LV Caterpillar G3306-GIDG_A022 | Check fan belt condition | 2 | M | 4 | 00 |  |  | 2231773.docx
Gidgealpa Gas Satellite - Power Generation - LV Alternator Package A Unit 554 | GIDG PWR GEN 1010-G-001A | 1010-G-001A | Alternator-LV Caterpillar G3306-GIDG_A021 | Lubricate fan drive & Idler pulley | 2 | M | 4 | 00 |  |  | 2231773.docx
Gidgealpa Gas Satellite - Power Generation - LV Alternator Package A Unit 554 | GIDG PWR GEN 1010-G-001A | 1010-G-001A | Alternator-LV Caterpillar G3306-GIDG_A015 | Clean oil header tank sight glasses & breather | 2 | M | 4 | 00 |  |  | 2231773.docx
Gidgealpa Gas Satellite - Power Generation - LV Alternator Package A Unit 554 | GIDG PWR GEN 1010-G-001A | 1010-G-001A | Alternator-LV Caterpillar G3306-GIDG_A055 | Re-dose coolant if required | 1 | Y | 4 | 00 |  |  | 2232756.docx
Gidgealpa Gas Satellite - Power Generation - LV Alternator Package A Unit 554 | GIDG PWR GEN 1010-G-001A | 1010-G-001A | Alternator-LV Caterpillar G3306-GIDG_A058 | Carry Out Top End Overhaul | 3 | Y | 4 | 00 |  |  | 2256646.docx
Gidgealpa Gas Satellite - Power Generation - LV Alternator Package A Unit 554 | GIDG PWR GEN 1010-G-001A | 1010-G-001A | Alternator-LV Caterpillar G3306-GIDG_A057 | Carry out Unit Overhaul | 3 | Y | 4 | 00 |  |  | 2222484.docx | 001
Gidgealpa Gas Satellite - Power Generation - LV Alternator Package A Unit 554 | GIDG PWR GEN 1010-G-001A | 1010-G-001A | Alternator-LV Caterpillar G3306-GIDG_A054 | Test coolant using Nalco kit | 1 | Y | 4 | 00 |  |  | 2232756.docx
Gidgealpa Gas Satellite - Power Generation - LV Alternator Package A Unit 554 | GIDG PWR GEN 1010-G-001A | 1010-G-001A | Alternator-LV Caterpillar G3306-GIDG_A048 | Clean filter housing | 1 | Y | 4 | 00 |  |  | 2232756.docx | 001
Gidgealpa Gas Satellite - Power Generation - LV Alternator Package A Unit 554 | GIDG PWR GEN 1010-G-001A | 1010-G-001A | Alternator-LV Caterpillar G3306-GIDG_A052 | Remove leads from coils & check for corrosion | 1 | Y | 4 | 00 |  |  | 2232756.docx
Gidgealpa Gas Satellite - Power Generation - LV Alternator Package A Unit 554 | GIDG PWR GEN 1010-G-001A | 1010-G-001A | Alternator-LV Caterpillar G3306-GIDG_A050 | Replace radiator cap | 1 | Y | 4 | 00 |  |  | 2232756.docx | 001
Gidgealpa Gas Satellite - Power Generation - LV Alternator Package A Unit 554 | GIDG PWR GEN 1010-G-001A | 1010-G-001A | Alternator-LV Caterpillar G3306-GIDG_A012 | Inspect filter condition and clean or replace as required | 2 | M | 4 | 00 |  |  | 2231773.docx | 001
Gidgealpa Gas Satellite - Power Generation - LV Alternator Package A Unit 554 | GIDG PWR GEN 1010-G-001A | 1010-G-001A | Alternator-LV Caterpillar G3306-GIDG_A010 | Replace oil filter | 2 | M | 4 | 00 |  |  | 2231773.docx
Gidgealpa Gas Satellite - Power Generation - LV Alternator Package A Unit 554 | GIDG PWR GEN 1010-G-001A | 1010-G-001A | Alternator-LV Caterpillar G3306-GIDG_A09 | Take oil sample | 2 | M | 4 | 00 |  |  | 2231773.docx
Gidgealpa Gas Satellite - Power Generation - LV Alternator Package A Unit 554 | GIDG PWR GEN 1010-G-001A | 1010-G-001A | Alternator-LV Caterpillar G3306-GIDG_A07 | Change oil using drain valves | 2 | M | 4 | 00 |  |  | 2231773.docx
Gidgealpa Gas Satellite - Power Generation - LV Alternator Package A Unit 554 | GIDG PWR GEN 1010-G-001A | 1010-G-001A | Alternator-LV Caterpillar G3306-GIDG_A08 | Re-fit plugs and close drain line valves | 2 | M | 4 | 00 |  |  | 2231773.docx
Gidgealpa Gas Satellite - Power Generation - LV Alternator Package A Unit 554 | GIDG PWR GEN 1010-G-001A | 1010-G-001A | Alternator-LV Caterpillar G3306-GIDG_A049 | Replace spark plugs | 1 | Y | 4 | 00 |  |  | 2232756.docx
Gidgealpa Gas Satellite - Power Generation - LV Alternator Package A Unit 554 | GIDG PWR GEN 1010-G-001A | 1010-G-001A | Alternator-LV Caterpillar G3306-GIDG_A013 | Clean filter and housing | 2 | M | 4 | 00 |  |  | 2231773.docx
Gidgealpa Gas Satellite - Power Generation - LV Alternator Package A Unit 554 | GIDG PWR GEN 1010-G-001A | 1010-G-001A | Alternator-LV Caterpillar G3306-GIDG_A011 | Re-fill sump with new oil to correct level | 2 | M | 4 | 00 |  |  | 2231773.docx
Gidgealpa Gas Satellite - Power Generation - LV Alternator Package A Unit 554 | GIDG PWR GEN 1010-G-001A | 1010-G-001A | Alternator-LV Caterpillar G3306-GIDG_A041 | Inspect wiring | 6 | M | 4 | 00 |  |  | 2232574.docx
Gidgealpa Gas Satellite - Power Generation - LV Alternator Package A Unit 554 | GIDG PWR GEN 1010-G-001A | 1010-G-001A | Alternator-LV Caterpillar G3306-GIDG_A037 | Check wiring continuity and resistance in activated and non-activated state | 6 | M | 4 | 00 |  |  | 2232159.docx
Gidgealpa Gas Satellite - Power Generation - LV Alternator Package A Unit 554 | GIDG PWR GEN 1010-G-001A | 1010-G-001A | Alternator-LV Caterpillar G3306-GIDG_A017 | Remove battery cables at battery | 2 | M | 4 | 00 |  |  | 2231773.docx
Gidgealpa Gas Satellite - Power Generation - LV Alternator Package A Unit 554 | GIDG PWR GEN 1010-G-001A | 1010-G-001A | Alternator-LV Caterpillar G3306-GIDG_A035 | Check all exposed wiring for chaffing | 6 | M | 4 | 00 |  |  | 2232159.docx
Gidgealpa Gas Satellite - Power Generation - LV Alternator Package A Unit 554 | GIDG PWR GEN 1010-G-001A | 1010-G-001A | Alternator-LV Caterpillar G3306-GIDG_A018 | Clean positive and negative battery terminals and cable connectors with wire brush | 2 | M | 4 | 00 |  |  | 2231773.docx
Gidgealpa Gas Satellite - Power Generation - LV Alternator Package A Unit 554 | GIDG PWR GEN 1010-G-001A | 1010-G-001A | Alternator-LV Caterpillar G3306-GIDG_A019 | Check terminal and connector for corrosion and condition | 2 | M | 4 | 00 |  |  | 2231773.docx
Gidgealpa Gas Satellite - Power Generation - LV Alternator Package B Unit 555 | GIDG PWR GEN 1010-G-001B | 1010-G-001B | Alternator-LV Caterpillar G3306-GIDG_A020 | Ensure terminals are tight and apply battery protector | 2 | M | 4 | 00 |  |  | 2231773.docx
Gidgealpa Gas Satellite - Power Generation - LV Alternator Package B Unit 555 | GIDG PWR GEN 1010-GX-001B | 1010-GX-001B | Alternator-LV Package IE Caterpillar G3306-GIDG_A081 | Check battery terminals for corrosion | 1 | Y | 01 | 00 |  |  | 2219764.docx
Gidgealpa Gas Satellite - Power Generation - LV Alternator Package B Unit 555 | GIDG PWR GEN 1010-GX-001B | 1010-GX-001B | Alternator-LV Package IE Caterpillar G3306-GIDG_A078 | Inspect power cabling from the Alternator to the circuit breaker | 1 | Y | 01 | 00 |  |  | 2219764.docx
Gidgealpa Gas Satellite - Power Generation - LV Alternator Package B Unit 555 | GIDG PWR GEN 1010-GX-001B | 1010-GX-001B | Alternator-LV Package IE Caterpillar G3306-GIDG_A062 | Inspect external Earth connections at Alternator Main Terminal Box for signs of corrosion and check earth cable connections for tightness | 1 | Y | 01 | 00 |  |  | 2219764.docx
Gidgealpa Gas Satellite - Power Generation - LV Alternator Package B Unit 555 | GIDG PWR GEN 1010-GX-001B | 1010-GX-001B | Alternator-LV Package IE Caterpillar G3306-GIDG_A074 | Inspect the Unit Control Panel door gasket for signs of dust ingress or gaskets damage | 1 | Y | 01 | 00 |  |  | 2219764.docx
Gidgealpa Gas Satellite - Power Generation - LV Alternator Package B Unit 555 | GIDG PWR GEN 1010-GX-001B | 1010-GX-001B | Alternator-LV Package IE Caterpillar G3306-GIDG_A064 | Inspect all Alternator External Earth connections for signs of corrosion and check earth cable connections for tightness | 1 | Y | 01 | 00 |  |  | 2219764.docx
Gidgealpa Gas Satellite - Power Generation - LV Alternator Package B Unit 555 | GIDG PWR GEN 1010-GX-001B | 1010-GX-001B | Alternator-LV Package IE Caterpillar G3306-GIDG_A070 | Inspect all electronic components and potentiometers on the AVR for signs of heat discolouration | 1 | Y | 01 | 00 |  |  | 2219764.docx
Gidgealpa Gas Satellite - Power Generation - LV Alternator Package B Unit 555 | GIDG PWR GEN 1010-GX-001B | 1010-GX-001B | Alternator-LV Package IE Caterpillar G3306-GIDG_A079 | Inspect power cabling for loose or missing supports, missing cable ties or contact with sharp edges / rough surfaces | 1 | Y | 01 | 00 |  |  | 2219764.docx
Gidgealpa Gas Satellite - Power Generation - LV Alternator Package B Unit 555 | GIDG PWR GEN 1010-GX-001B | 1010-GX-001B | Alternator-LV Package IE Caterpillar G3306-GIDG_A069 | Inspect exterior condition of AVR for damaged panels or missing screws | 1 | Y | 01 | 00 |  |  | 2219764.docx
Gidgealpa Gas Satellite - Power Generation - LV Alternator Package B Unit 555 | GIDG PWR GEN 1010-GX-001B | 1010-GX-001B | Alternator-LV Package IE Caterpillar G3306-GIDG_A061 | Inspect exterior of alternator unit for damage, missing bolts, missing or loose covers, missing cable ties, or a build up of oil or dust | 1 | Y | 01 | 00 |  |  | 2219764.docx
Gidgealpa Gas Satellite - Power Generation - LV Alternator Package B Unit 555 | GIDG PWR GEN 1010-GX-001B | 1010-GX-001B | Alternator-LV Package IE Caterpillar G3306-GIDG_A065 | Inspect condition of all Unit Control Panel buttons for damage that prevents normal operation | 1 | Y | 01 | 00 |  |  | 2219764.docx
Gidgealpa Gas Satellite - Power Generation - LV Alternator Package B Unit 555 | GIDG PWR GEN 1010-GX-001B | 1010-GX-001B | Alternator-LV Package IE Caterpillar G3306-GIDG_A063 | Clean off any corrosion and repair, re-terminate or tighten connection if required | 1 | Y | 01 | 00 |  |  | 2219764.docx
Gidgealpa Gas Satellite - Power Generation - LV Alternator Package B Unit 555 | GIDG PWR GEN 1010-GX-001B | 1010-GX-001B | Alternator-LV Package IE Caterpillar G3306-GIDG_A059 | Ensure all redundant items not required in the electrical panels | 1 | Y | 01 | 00 |  |  | 2219764.docx
Gidgealpa Gas Satellite - Power Generation - LV Alternator Package B Unit 555 | GIDG PWR GEN 1010-GX-001B | 1010-GX-001B | Alternator-LV Package IE Caterpillar G3306-GIDG_A060 | Check Electrical Hazard Warning signs to ensure they are securely mounted and legible | 1 | Y | 01 | 00 |  |  | 2219764.docx
Gidgealpa Gas Satellite - Power Generation - LV Alternator Package B Unit 555 | GIDG PWR GEN 1010-GX-001B | 1010-GX-001B | Alternator-LV Package IE Caterpillar G3306-GIDG_A072 | Inspect all other terminals and circuit wiring connections on the Unit Control Panel for signs of heat discolouration | 1 | Y | 01 | 00 |  |  | 2219764.docx
Gidgealpa Gas Satellite - Power Generation - LV Alternator Package B Unit 555 | GIDG PWR GEN 1010-GX-001B | 1010-GX-001B | Alternator-LV Package IE Caterpillar G3306-GIDG_A077 | Clean off all expelled grease | 1 | Y | 01 | 00 |  |  | 2219764.docx
Gidgealpa Gas Satellite - Power Generation - LV Alternator Package B Unit 555 | GIDG PWR GEN 1010-GX-001B | 1010-GX-001B | Alternator-LV Package IE Caterpillar G3306-GIDG_A067 | Inspect terminals and circuit wiring connections on the AVR unit for signs of heat discolouration | 1 | Y | 01 | 00 |  |  | 2219764.docx
Gidgealpa Gas Satellite - Power Generation - LV Alternator Package B Unit 555 | GIDG PWR GEN 1010-GX-001B | 1010-GX-001B | Alternator-LV Package IE Caterpillar G3306-GIDG_A071 | Check the AVR heat sink cooling fins for build up of dust, clean as required | 1 | Y | 01 | 00 |  |  | 2219764.docx
Gidgealpa Gas Satellite - Power Generation - LV Alternator Package B Unit 555 | GIDG PWR GEN 1010-GX-001B | 1010-GX-001B | Alternator-LV Package IE Caterpillar G3306-GIDG_A080 | Check battery electrolyte level in each cell, top up if required with de-min water | 1 | Y | 01 | 00 |  |  | 2219764.docx
Gidgealpa Gas Satellite - Power Generation - LV Alternator Package B Unit 555 | GIDG PWR GEN 1010-GX-001B | 1010-GX-001B | Alternator-LV Package IE Caterpillar G3306-GIDG_A073 | Clean and vacuum the Unit Control Panel control cabinet, ensure all heat sink cooling fins are clean | 1 | Y | 01 | 00 |  |  | 2219764.docx
Gidgealpa Gas Satellite - Power Generation - LV Alternator Package B Unit 555 | GIDG PWR GEN 1010-GX-001B | 1010-GX-001B | Alternator-LV Package IE Caterpillar G3306-GIDG_A075 | Check the circuit breaker fixing bolts for tighness | 1 | Y | 01 | 00 |  |  | 2219764.docx
Gidgealpa Gas Satellite - Power Generation - LV Alternator Package B Unit 555 | GIDG PWR GEN 1010-GX-001B | 1010-GX-001B | Alternator-LV Package IE Caterpillar G3306-GIDG_A066 | Inspect the condition of all panel meters | 1 | Y | 01 | 00 |  |  | 2219764.docx | 001
Gidgealpa Gas Satellite - Power Generation - LV Alternator Package B Unit 555 | GIDG PWR GEN 1010-GX-001B | 1010-GX-001B | Alternator-LV Package IE Caterpillar G3306-GIDG_A068 | Check the security of the connections by applying force to the wires | 1 | Y | 01 | 00 |  |  | 2219764.docx
Gidgealpa Gas Satellite - Power Generation - LV Alternator Package B Unit 555 | GIDG PWR GEN 1010-GX-001B | 1010-GX-001B | Alternator-LV Package IE Caterpillar G3306-GIDG_A076 | Lubricate Alternator Bearings | 1 | Y | 01 | 00 |  |  | 2219764.docx
Gidgealpa Gas Satellite - Power Generation - LV Alternator Package B Unit 555 | GIDG PWR GEN 1010-GX-001B | 1010-GX-001B | Alternator-LV Package IE Caterpillar G3306-GIDG_A083 | Inspect the condition of all charger panel meters and ensure they operate as expected | 1 | Y | 01 | 00 |  |  | 2219764.docx
Gidgealpa Gas Satellite - Power Generation - LV Alternator Package B Unit 555 | GIDG PWR GEN 1010-GX-001B | 1010-GX-001B | Alternator-LV Package IE Caterpillar G3306-GIDG_A082 | Check the battery charger amp meter, float voltage and boost voltage for expected values | 1 | Y | 01 | 00 |  |  | 2219764.docx
Gidgealpa Gas Satellite - Power Generation - LV Alternator Package B Unit 555 | GIDG PWR GEN 1010-GE-001B | 1010-GE-001B | Alternator-LV Caterpillar G3306-GIDG_A032 | Inspect air intake hoses for deterioration or cracks | 6 | M | 4 | 00 |  |  | 2232159.docx | 001
Gidgealpa Gas Satellite - Power Generation - LV Alternator Package B Unit 555 | GIDG PWR GEN 1010-GE-001B | 1010-GE-001B | Alternator-LV Caterpillar G3306-GIDG_A033 | Inspect all coolant hoses and pipe joints for leaks | 6 | M | 4 | 00 |  |  | 2232159.docx
Gidgealpa Gas Satellite - Power Generation - LV Alternator Package B Unit 555 | GIDG PWR GEN 1010-GE-001B | 1010-GE-001B | Alternator-LV Caterpillar G3306-GIDG_A034 | Ensure hoses are in good condition | 6 | M | 4 | 00 |  |  | 2232159.docx
Gidgealpa Gas Satellite - Power Generation - LV Alternator Package B Unit 555 | GIDG PWR GEN 1010-GE-001B | 1010-GE-001B | Alternator-LV Caterpillar G3306-GIDG_A026 | Clean and remove any blockages | 2 | M | 4 | 00 |  |  | 2231773.docx
Gidgealpa Gas Satellite - Power Generation - LV Alternator Package B Unit 555 | GIDG PWR GEN 1010-GE-001B | 1010-GE-001B | Alternator-LV Caterpillar G3306-GIDG_A025 | Check radiator cores for blockage | 2 | M | 4 | 00 |  |  | 2231773.docx
Gidgealpa Gas Satellite - Power Generation - LV Alternator Package B Unit 555 | GIDG PWR GEN 1010-GE-001B | 1010-GE-001B | Alternator-LV Caterpillar G3306-GIDG_A051 | Remove and clean engine oil auto leveller | 1 | Y | 4 | 00 |  |  | 2232756.docx
Gidgealpa Gas Satellite - Power Generation - LV Alternator Package B Unit 555 | GIDG PWR GEN 1010-GE-001B | 1010-GE-001B | Alternator-LV Caterpillar G3306-GIDG_A043 | Remove and replace the engine oil filter | 1 | Y | 4 | 00 |  |  | 2232756.docx
Gidgealpa Gas Satellite - Power Generation - LV Alternator Package B Unit 555 | GIDG PWR GEN 1010-GE-001B | 1010-GE-001B | Alternator-LV Caterpillar G3306-GIDG_A044 | Replace the engine drain plugs | 1 | Y | 4 | 00 |  |  | 2232756.docx
Gidgealpa Gas Satellite - Power Generation - LV Alternator Package B Unit 555 | GIDG PWR GEN 1010-GE-001B | 1010-GE-001B | Alternator-LV Caterpillar G3306-GIDG_A042 | Drain the oil from the engine | 1 | Y | 4 | 00 |  |  | 2232756.docx
Gidgealpa Gas Satellite - Power Generation - LV Alternator Package B Unit 555 | GIDG PWR GEN 1010-GE-001B | 1010-GE-001B | Alternator-LV Caterpillar G3306-GIDG_A02 | Check cooling system for leaks, check level and top up as required | 1 | W | 44 | 01 | 1010-GE-001B 1W-44-01- | 1010-GE-001B 1W-44-01- | OEC Tasks List
Gidgealpa Gas Satellite - Power Generation - LV Alternator Package B Unit 555 | GIDG PWR GEN 1010-GE-001B | 1010-GE-001B | Alternator-LV Caterpillar G3306-GIDG_A01 | Check engine oil levels, check for leaks | 1 | W | 44 | 01 | 1010-GE-001B 1W-44-01- | 1010-GE-001B 1W-44-01- | OEC Tasks List
Gidgealpa Gas Satellite - Power Generation - LV Alternator Package B Unit 555 | GIDG PWR GEN 1010-GE-001B | 1010-GE-001B | Alternator-LV Caterpillar G3306-GIDG_A045 | Fill the engine with oil | 1 | Y | 4 | 00 |  |  | 2232756.docx
Gidgealpa Gas Satellite - Power Generation - LV Alternator Package B Unit 555 | GIDG PWR GEN 1010-GE-001B | 1010-GE-001B | Alternator-LV Caterpillar G3306-GIDG_A019 | Check terminal and connector for corrosion and condition | 2 | M | 4 | 00 |  |  | 2231773.docx
Gidgealpa Gas Satellite - Power Generation - LV Alternator Package B Unit 555 | GIDG PWR GEN 1010-GE-001B | 1010-GE-001B | Alternator-LV Caterpillar G3306-GIDG_A018 | Clean positive and negative battery terminals and cable connectors with wire brush | 2 | M | 4 | 00 |  |  | 2231773.docx
Gidgealpa Gas Satellite - Power Generation - LV Alternator Package B Unit 555 | GIDG PWR GEN 1010-GE-001B | 1010-GE-001B | Alternator-LV Caterpillar G3306-GIDG_A020 | Ensure terminals are tight and apply battery protector | 2 | M | 4 | 00 |  |  | 2231773.docx
Gidgealpa Gas Satellite - Power Generation - LV Alternator Package B Unit 555 | GIDG PWR GEN 1010-GE-001B | 1010-GE-001B | Alternator-LV Caterpillar G3306-GIDG_A037 | Check wiring continuity and resistance in activated and non-activated state | 6 | M | 4 | 00 |  |  | 2232159.docx
Gidgealpa Gas Satellite - Power Generation - LV Alternator Package B Unit 555 | GIDG PWR GEN 1010-GE-001B | 1010-GE-001B | Alternator-LV Caterpillar G3306-GIDG_A035 | Check all exposed wiring for chaffing | 6 | M | 4 | 00 |  |  | 2232159.docx
Gidgealpa Gas Satellite - Power Generation - LV Alternator Package B Unit 555 | GIDG PWR GEN 1010-GE-001B | 1010-GE-001B | Alternator-LV Caterpillar G3306-GIDG_A017 | Remove battery cables at battery | 2 | M | 4 | 00 |  |  | 2231773.docx
Gidgealpa Gas Satellite - Power Generation - LV Alternator Package B Unit 555 | GIDG PWR GEN 1010-GE-001B | 1010-GE-001B | Alternator-LV Caterpillar G3306-GIDG_A041 | Inspect wiring | 6 | M | 4 | 00 |  |  | 2232574.docx
Gidgealpa Gas Satellite - Power Generation - LV Alternator Package B Unit 555 | GIDG PWR GEN 1010-GE-001B | 1010-GE-001B | Alternator-LV Caterpillar G3306-GIDG_A010 | Replace oil filter | 2 | M | 4 | 00 |  |  | 2231773.docx
Gidgealpa Gas Satellite - Power Generation - LV Alternator Package B Unit 555 | GIDG PWR GEN 1010-GE-001B | 1010-GE-001B | Alternator-LV Caterpillar G3306-GIDG_A055 | Re-dose coolant if required | 1 | Y | 4 | 00 |  |  | 2232756.docx
Gidgealpa Gas Satellite - Power Generation - LV Alternator Package B Unit 555 | GIDG PWR GEN 1010-GE-001B | 1010-GE-001B | Alternator-LV Caterpillar G3306-GIDG_A07 | Change oil using drain valves | 2 | M | 4 | 00 |  |  | 2231773.docx
Gidgealpa Gas Satellite - Power Generation - LV Alternator Package B Unit 555 | GIDG PWR GEN 1010-GE-001B | 1010-GE-001B | Alternator-LV Caterpillar G3306-GIDG_A012 | Inspect filter condition and clean or replace as required | 2 | M | 4 | 00 |  |  | 2231773.docx
Gidgealpa Gas Satellite - Power Generation - LV Alternator Package B Unit 555 | GIDG PWR GEN 1010-GE-001B | 1010-GE-001B | Alternator-LV Caterpillar G3306-GIDG_A027 | Adjust valve lash / tappets | 2 | M | 4 | 00 |  |  | 2231773.docx
Gidgealpa Gas Satellite - Power Generation - LV Alternator Package B Unit 555 | GIDG PWR GEN 1010-GE-001B | 1010-GE-001B | Alternator-LV Caterpillar G3306-GIDG_A03 | Check air filter blockage indicators, air cooling system water flow | 1 | W | 44 | 01 | 1010-GE-001B 1W-44-01- | 1010-GE-001B 1W-44-01- | OEC Tasks List
Gidgealpa Gas Satellite - Power Generation - LV Alternator Package B Unit 555 | GIDG PWR GEN 1010-GE-001B | 1010-GE-001B | Alternator-LV Caterpillar G3306-GIDG_A053 | Clean and remove any corrosion buildup | 1 | Y | 4 | 00 |  |  | 2232756.docx
Gidgealpa Gas Satellite - Power Generation - LV Alternator Package B Unit 555 | GIDG PWR GEN 1010-GE-001B | 1010-GE-001B | Alternator-LV Caterpillar G3306-GIDG_A052 | Remove leads from coils & check for corrosion | 1 | Y | 4 | 00 |  |  | 2232756.docx
Gidgealpa Gas Satellite - Power Generation - LV Alternator Package B Unit 555 | GIDG PWR GEN 1010-GE-001B | 1010-GE-001B | Alternator-LV Caterpillar G3306-GIDG_A011 | Re-fill sump with new oil to correct level | 2 | M | 4 | 00 |  |  | 2231773.docx
Gidgealpa Gas Satellite - Power Generation - LV Alternator Package B Unit 555 | GIDG PWR GEN 1010-GE-001B | 1010-GE-001B | Alternator-LV Caterpillar G3306-GIDG_A048 | Clean filter housing | 1 | Y | 4 | 00 |  |  | 2232756.docx
Gidgealpa Gas Satellite - Power Generation - LV Alternator Package B Unit 555 | GIDG PWR GEN 1010-GE-001B | 1010-GE-001B | Alternator-LV Caterpillar G3306-GIDG_A08 | Re-fit plugs and close drain line valves | 2 | M | 4 | 00 |  |  | 2231773.docx
Gidgealpa Gas Satellite - Power Generation - LV Alternator Package B Unit 555 | GIDG PWR GEN 1010-GE-001B | 1010-GE-001B | Alternator-LV Caterpillar G3306-GIDG_A049 | Replace spark plugs | 1 | Y | 4 | 00 |  |  | 2232756.docx
Gidgealpa Gas Satellite - Power Generation - LV Alternator Package B Unit 555 | GIDG PWR GEN 1010-GE-001B | 1010-GE-001B | Alternator-LV Caterpillar G3306-GIDG_A054 | Test coolant using Nalco kit | 1 | Y | 4 | 00 |  |  | 2232756.docx
Gidgealpa Gas Satellite - Power Generation - LV Alternator Package B Unit 555 | GIDG PWR GEN 1010-GE-001B | 1010-GE-001B | Alternator-LV Caterpillar G3306-GIDG_A050 | Replace radiator cap | 1 | Y | 4 | 00 |  |  | 2232756.docx
Gidgealpa Gas Satellite - Power Generation - LV Alternator Package B Unit 555 | GIDG PWR GEN 1010-GE-001B | 1010-GE-001B | Alternator-LV Caterpillar G3306-GIDG_A09 | Take oil sample | 2 | M | 4 | 00 |  |  | 2231773.docx
Gidgealpa Gas Satellite - Power Generation - LV Alternator Package B Unit 555 | GIDG PWR GEN 1010-GE-001B | 1010-GE-001B | Alternator-LV Caterpillar G3306-GIDG_A058 | Carry Out Top End Overhaul | 3 | Y | 4 | 00 |  |  | 2256646.docx
Gidgealpa Gas Satellite - Power Generation - LV Alternator Package B Unit 555 | GIDG PWR GEN 1010-GE-001B | 1010-GE-001B | Alternator-LV Caterpillar G3306-GIDG_A013 | Clean filter and housing | 2 | M | 4 | 00 |  |  | 2231773.docx
Gidgealpa Gas Satellite - Power Generation - LV Alternator Package B Unit 555 | GIDG PWR GEN 1010-GE-001B | 1010-GE-001B | Alternator-LV Caterpillar G3306-GIDG_A057 | Carry out Unit Overhaul | 3 | Y | 4 | 00 |  |  | 2222484.docx
Gidgealpa Gas Satellite - Power Generation - LV Alternator Package B Unit 555 | GIDG PWR GEN 1010-GE-001B | 1010-GE-001B | Alternator-LV Caterpillar G3306-GIDG_A024 | Check coolant level | 2 | M | 4 | 00 |  |  | 2231773.docx
Gidgealpa Gas Satellite - Power Generation - LV Alternator Package B Unit 555 | GIDG PWR GEN 1010-GE-001B | 1010-GE-001B | Alternator-LV Caterpillar G3306-GIDG_A016 | Check the electrolyte level in the batteries and top up as required | 2 | M | 4 | 00 |  |  | 2231773.docx
Gidgealpa Gas Satellite - Power Generation - LV Alternator Package B Unit 555 | GIDG PWR GEN 1010-GE-001B | 1010-GE-001B | Alternator-LV Caterpillar G3306-GIDG_A023 | Replace fan belt or alternator belt | 2 | M | 4 | 00 |  |  | 2231773.docx
Gidgealpa Gas Satellite - Power Generation - LV Alternator Package B Unit 555 | GIDG PWR GEN 1010-GE-001B | 1010-GE-001B | Alternator-LV Caterpillar G3306-GIDG_A022 | Check fan belt condition | 2 | M | 4 | 00 |  |  | 2231773.docx
Gidgealpa Gas Satellite - Power Generation - LV Alternator Package B Unit 555 | GIDG PWR GEN 1010-GE-001B | 1010-GE-001B | Alternator-LV Caterpillar G3306-GIDG_A030 | Clean crankcase breather | 2 | M | 4 | 00 |  |  | 2231773.docx
Gidgealpa Gas Satellite - Power Generation - LV Alternator Package B Unit 555 | GIDG PWR GEN 1010-GE-001B | 1010-GE-001B | Alternator-LV Caterpillar G3306-GIDG_A014 | Replace air filter element and clean housing | 2 | M | 4 | 00 |  |  | 2231773.docx | 001
Gidgealpa Gas Satellite - Power Generation - LV Alternator Package B Unit 555 | GIDG PWR GEN 1010-GE-001B | 1010-GE-001B | Alternator-LV Caterpillar G3306-GIDG_A028 | Check and adjust intake and exhaust valve lash | 2 | M | 4 | 00 |  |  | 2231773.docx | 001
Gidgealpa Gas Satellite - Power Generation - LV Alternator Package B Unit 555 | GIDG PWR GEN 1010-GE-001B | 1010-GE-001B | Alternator-LV Caterpillar G3306-GIDG_A040 | Ensure alignment of drive has not altered If replacements or re-tensioning | 6 | M | 4 | 00 |  |  | 2232574.docx
Gidgealpa Gas Satellite - Power Generation - LV Alternator Package B Unit 555 | GIDG PWR GEN 1010-GE-001B | 1010-GE-001B | Alternator-LV Caterpillar G3306-GIDG_A031 | Lubricate carburettor linkage | 2 | M | 4 | 00 |  |  | 2231773.docx
Gidgealpa Gas Satellite - Power Generation - LV Alternator Package B Unit 555 | GIDG PWR GEN 1010-GE-001B | 1010-GE-001B | Alternator-LV Caterpillar G3306-GIDG_A015 | Clean oil header tank sight glasses & breather | 2 | M | 4 | 00 |  |  | 2231773.docx
Gidgealpa Gas Satellite - Power Generation - LV Alternator Package B Unit 555 | GIDG PWR GEN 1010-GE-001B | 1010-GE-001B | Alternator-LV Caterpillar G3306-GIDG_A029 | Re-fit existing rocker cover gasket and tension rocker cover | 2 | M | 4 | 00 |  |  | 2231773.docx
Gidgealpa Gas Satellite - Power Generation - LV Alternator Package B Unit 555 | GIDG PWR GEN 1010-GE-001B | 1010-GE-001B | Alternator-LV Caterpillar G3306-GIDG_A047 | Replace air filter element | 1 | Y | 4 | 00 |  |  | 2232756.docx
Gidgealpa Gas Satellite - Power Generation - LV Alternator Package B Unit 555 | GIDG PWR GEN 1010-GE-001B | 1010-GE-001B | Alternator-LV Caterpillar G3306-GIDG_A021 | Lubricate fan drive & Idler pulley | 2 | M | 4 | 00 |  |  | 2231773.docx
Gidgealpa Gas Satellite - Power Generation - LV Alternator Package B Unit 555 | GIDG PWR GEN 1010-GE-001B | 1010-GE-001B | Alternator-LV Caterpillar G3306-GIDG_A038 | Lubricate rear alternator bearing | 6 | M | 4 | 00 |  |  | 2232159.docx
Gidgealpa Gas Satellite - Power Generation - LV Alternator Package B Unit 555 | GIDG PWR GEN 1010-GE-001B | 1010-GE-001B | Alternator-LV Caterpillar G3306-GIDG_A06 | For Emergency Diesel Generator, Check diesel Fuel level | 1 | W | 44 | 01 | 1010-GE-001B 1W-44-01- | 1010-GE-001B 1W-44-01- | OEC Tasks List
Gidgealpa Gas Satellite - Power Generation - LV Alternator Package B Unit 555 | GIDG PWR GEN 1010-GE-001B | 1010-GE-001B | Alternator-LV Caterpillar G3306-GIDG_A046 | Inspect the engine fill and drain points for visible oil leaks, clean and repair as required | 1 | Y | 4 | 00 |  |  | 2232756.docx
Gidgealpa Gas Satellite - Power Generation - LV Alternator Package B Unit 555 | GIDG PWR GEN 1010-GE-001B | 1010-GE-001B | Alternator-LV Caterpillar G3306-GIDG_A05 | For Emergency Diesel Generator, Start the set and run to check running condition | 1 | W | 44 | 01 | 1010-GE-001B 1W-44-01- | 1010-GE-001B 1W-44-01- | OEC Tasks List
Gidgealpa Gas Satellite - Power Generation - LV Alternator Package B Unit 555 | GIDG PWR GEN 1010-GE-001B | 1010-GE-001B | Alternator-LV Caterpillar G3306-GIDG_A04 | Check for abnormal noise from engine | 1 | W | 44 | 01 | 1010-GE-001B 1W-44-01- | 1010-GE-001B 1W-44-01- | OEC Tasks List
Gidgealpa Gas Satellite - Power Generation - LV Alternator Package B Unit 555 | GIDG PWR GEN 1010-GE-001B | 1010-GE-001B | Alternator-LV Caterpillar G3306-GIDG_A039 | Inspect engine mounts for cracks or looseness | 6 | M | 4 | 00 |  |  | 2232574.docx | 001
Gidgealpa Gas Satellite - Power Generation - LV Alternator Package B Unit 555 | GIDG PWR GEN 1010-GE-001B | 1010-GE-001B | Alternator-LV Caterpillar G3306-GIDG_A056 | Replace cylinder head temp shutdown switch | 1 | Y | 01 | 00 |  |  | 2232756.docx
Gidgealpa Gas Satellite - Power Generation - LV Alternator Package B Unit 555 | GIDG PWR GEN 1010-GE-001B | 1010-GE-001B | Alternator-LV Caterpillar G3306-GIDG_A036 | Function test oil press low shutdown switch | 6 | M | 4 | 00 |  |  | 2232159.docx
Gidgealpa Gas Satellite - Power Generation - LV Alternator Package B Unit 555 | GIDG PWR GEN 1010-G-001B | 1010-G-001B | Alternator-LV Caterpillar G3306-GIDG_A025 | Check radiator cores for blockage | 2 | M | 4 | 00 |  |  | 2231773.docx
Gidgealpa Gas Satellite - Power Generation - LV Alternator Package B Unit 555 | GIDG PWR GEN 1010-G-001B | 1010-G-001B | Alternator-LV Caterpillar G3306-GIDG_A033 | Inspect all coolant hoses and pipe joints for leaks | 6 | M | 4 | 00 |  |  | 2232159.docx
Gidgealpa Gas Satellite - Power Generation - LV Alternator Package B Unit 555 | GIDG PWR GEN 1010-G-001B | 1010-G-001B | Alternator-LV Caterpillar G3306-GIDG_A026 | Clean and remove any blockages | 2 | M | 4 | 00 |  |  | 2231773.docx
Gidgealpa Gas Satellite - Power Generation - LV Alternator Package B Unit 555 | GIDG PWR GEN 1010-G-001B | 1010-G-001B | Alternator-LV Caterpillar G3306-GIDG_A034 | Ensure hoses are in good condition | 6 | M | 4 | 00 |  |  | 2232159.docx
Gidgealpa Gas Satellite - Power Generation - LV Alternator Package B Unit 555 | GIDG PWR GEN 1010-G-001B | 1010-G-001B | Alternator-LV Caterpillar G3306-GIDG_A032 | Inspect air intake hoses for deterioration or cracks | 6 | M | 4 | 00 |  |  | 2232159.docx
Gidgealpa Gas Satellite - Power Generation - LV Alternator Package B Unit 555 | GIDG PWR GEN 1010-G-001B | 1010-G-001B | Alternator-LV Caterpillar G3306-GIDG_A038 | Lubricate rear alternator bearing | 6 | M | 4 | 00 |  |  | 2232159.docx
Gidgealpa Gas Satellite - Power Generation - LV Alternator Package B Unit 555 | GIDG PWR GEN 1010-G-001B | 1010-G-001B | Alternator-LV Caterpillar G3306-GIDG_A036 | Function test oil press low shutdown switch | 6 | M | 4 | 00 |  |  | 2232159.docx
Gidgealpa Gas Satellite - Power Generation - LV Alternator Package B Unit 555 | GIDG PWR GEN 1010-G-001B | 1010-G-001B | Alternator-LV Caterpillar G3306-GIDG_A056 | Replace cylinder head temp shutdown switch | 1 | Y | 01 | 00 |  |  | 2232756.docx
Gidgealpa Gas Satellite - Power Generation - LV Alternator Package B Unit 555 | GIDG PWR GEN 1010-G-001B | 1010-G-001B | Alternator-LV Caterpillar G3306-GIDG_A02 | Check cooling system for leaks, check level and top up as required | 1 | W | 44 | 01 | 1010-G-001B 1W-44-01- | 1010-G-001B 1W-44-01- | OEC Tasks List
Gidgealpa Gas Satellite - Power Generation - LV Alternator Package B Unit 555 | GIDG PWR GEN 1010-G-001B | 1010-G-001B | Alternator-LV Caterpillar G3306-GIDG_A042 | Drain the oil from the engine | 1 | Y | 4 | 00 |  |  | 2232756.docx
Gidgealpa Gas Satellite - Power Generation - LV Alternator Package B Unit 555 | GIDG PWR GEN 1010-G-001B | 1010-G-001B | Alternator-LV Caterpillar G3306-GIDG_A043 | Remove and replace the engine oil filter | 1 | Y | 4 | 00 |  |  | 2232756.docx
Gidgealpa Gas Satellite - Power Generation - LV Alternator Package B Unit 555 | GIDG PWR GEN 1010-G-001B | 1010-G-001B | Alternator-LV Caterpillar G3306-GIDG_A045 | Fill the engine with oil | 1 | Y | 4 | 00 |  |  | 2232756.docx
Gidgealpa Gas Satellite - Power Generation - LV Alternator Package B Unit 555 | GIDG PWR GEN 1010-G-001B | 1010-G-001B | Alternator-LV Caterpillar G3306-GIDG_A044 | Replace the engine drain plugs | 1 | Y | 4 | 00 |  |  | 2232756.docx
Gidgealpa Gas Satellite - Power Generation - LV Alternator Package B Unit 555 | GIDG PWR GEN 1010-G-001B | 1010-G-001B | Alternator-LV Caterpillar G3306-GIDG_A051 | Remove and clean engine oil auto leveller | 1 | Y | 4 | 00 |  |  | 2232756.docx
Gidgealpa Gas Satellite - Power Generation - LV Alternator Package B Unit 555 | GIDG PWR GEN 1010-G-001B | 1010-G-001B | Alternator-LV Caterpillar G3306-GIDG_A01 | Check engine oil levels, check for leaks | 1 | W | 44 | 01 | 1010-G-001B 1W-44-01- | 1010-G-001B 1W-44-01- | OEC Tasks List
Gidgealpa Gas Satellite - Power Generation - LV Alternator Package B Unit 555 | GIDG PWR GEN 1010-G-001B | 1010-G-001B | Alternator-LV Caterpillar G3306-GIDG_A03 | Check air filter blockage indicators, air cooling system water flow | 1 | W | 44 | 01 | 1010-G-001B 1W-44-01- | 1010-G-001B 1W-44-01- | OEC Tasks List
Gidgealpa Gas Satellite - Power Generation - LV Alternator Package B Unit 555 | GIDG PWR GEN 1010-G-001B | 1010-G-001B | Alternator-LV Caterpillar G3306-GIDG_A024 | Check coolant level | 2 | M | 4 | 00 |  |  | 2231773.docx
Gidgealpa Gas Satellite - Power Generation - LV Alternator Package B Unit 555 | GIDG PWR GEN 1010-G-001B | 1010-G-001B | Alternator-LV Caterpillar G3306-GIDG_A027 | Adjust valve lash / tappets | 2 | M | 4 | 00 |  |  | 2231773.docx
Gidgealpa Gas Satellite - Power Generation - LV Alternator Package B Unit 555 | GIDG PWR GEN 1010-G-001B | 1010-G-001B | Alternator-LV Caterpillar G3306-GIDG_A053 | Clean and remove any corrosion buildup | 1 | Y | 4 | 00 |  |  | 2232756.docx
Gidgealpa Gas Satellite - Power Generation - LV Alternator Package B Unit 555 | GIDG PWR GEN 1010-G-001B | 1010-G-001B | Alternator-LV Caterpillar G3306-GIDG_A023 | Replace fan belt or alternator belt | 2 | M | 4 | 00 |  |  | 2231773.docx
Gidgealpa Gas Satellite - Power Generation - LV Alternator Package B Unit 555 | GIDG PWR GEN 1010-G-001B | 1010-G-001B | Alternator-LV Caterpillar G3306-GIDG_A014 | Replace air filter element and clean housing | 2 | M | 4 | 00 |  |  | 2231773.docx
Gidgealpa Gas Satellite - Power Generation - LV Alternator Package B Unit 555 | GIDG PWR GEN 1010-G-001B | 1010-G-001B | Alternator-LV Caterpillar G3306-GIDG_A030 | Clean crankcase breather | 2 | M | 4 | 00 |  |  | 2231773.docx
Gidgealpa Gas Satellite - Power Generation - LV Alternator Package B Unit 555 | GIDG PWR GEN 1010-G-001B | 1010-G-001B | Alternator-LV Caterpillar G3306-GIDG_A016 | Check the electrolyte level in the batteries and top up as required | 2 | M | 4 | 00 |  |  | 2231773.docx
Gidgealpa Gas Satellite - Power Generation - LV Alternator Package B Unit 555 | GIDG PWR GEN 1010-G-001B | 1010-G-001B | Alternator-LV Caterpillar G3306-GIDG_A040 | Ensure alignment of drive has not altered If replacements or re-tensioning | 6 | M | 4 | 00 |  |  | 2232574.docx | 001
Gidgealpa Gas Satellite - Power Generation - LV Alternator Package B Unit 555 | GIDG PWR GEN 1010-G-001B | 1010-G-001B | Alternator-LV Caterpillar G3306-GIDG_A047 | Replace air filter element | 1 | Y | 4 | 00 |  |  | 2232756.docx
Gidgealpa Gas Satellite - Power Generation - LV Alternator Package B Unit 555 | GIDG PWR GEN 1010-G-001B | 1010-G-001B | Alternator-LV Caterpillar G3306-GIDG_A031 | Lubricate carburettor linkage | 2 | M | 4 | 00 |  |  | 2231773.docx | 001
Gidgealpa Gas Satellite - Power Generation - LV Alternator Package B Unit 555 | GIDG PWR GEN 1010-G-001B | 1010-G-001B | Alternator-LV Caterpillar G3306-GIDG_A028 | Check and adjust intake and exhaust valve lash | 2 | M | 4 | 00 |  |  | 2231773.docx | 001
Gidgealpa Gas Satellite - Power Generation - LV Alternator Package B Unit 555 | GIDG PWR GEN 1010-G-001B | 1010-G-001B | Alternator-LV Caterpillar G3306-GIDG_A029 | Re-fit existing rocker cover gasket and tension rocker cover | 2 | M | 4 | 00 |  |  | 2231773.docx
Gidgealpa Gas Satellite - Power Generation - LV Alternator Package B Unit 555 | GIDG PWR GEN 1010-G-001B | 1010-G-001B | Alternator-LV Caterpillar G3306-GIDG_A022 | Check fan belt condition | 2 | M | 4 | 00 |  |  | 2231773.docx
Gidgealpa Gas Satellite - Power Generation - LV Alternator Package B Unit 555 | GIDG PWR GEN 1010-G-001B | 1010-G-001B | Alternator-LV Caterpillar G3306-GIDG_A021 | Lubricate fan drive & Idler pulley | 2 | M | 4 | 00 |  |  | 2231773.docx
Gidgealpa Gas Satellite - Power Generation - LV Alternator Package B Unit 555 | GIDG PWR GEN 1010-G-001B | 1010-G-001B | Alternator-LV Caterpillar G3306-GIDG_A015 | Clean oil header tank sight glasses & breather | 2 | M | 4 | 00 |  |  | 2231773.docx
Gidgealpa Gas Satellite - Power Generation - LV Alternator Package B Unit 555 | GIDG PWR GEN 1010-G-001B | 1010-G-001B | Alternator-LV Caterpillar G3306-GIDG_A055 | Re-dose coolant if required | 1 | Y | 4 | 00 |  |  | 2232756.docx
Gidgealpa Gas Satellite - Power Generation - LV Alternator Package B Unit 555 | GIDG PWR GEN 1010-G-001B | 1010-G-001B | Alternator-LV Caterpillar G3306-GIDG_A058 | Carry Out Top End Overhaul | 3 | Y | 4 | 00 |  |  | 2256646.docx
Gidgealpa Gas Satellite - Power Generation - LV Alternator Package B Unit 555 | GIDG PWR GEN 1010-G-001B | 1010-G-001B | Alternator-LV Caterpillar G3306-GIDG_A057 | Carry out Unit Overhaul | 3 | Y | 4 | 00 |  |  | 2222484.docx
Gidgealpa Gas Satellite - Power Generation - LV Alternator Package B Unit 555 | GIDG PWR GEN 1010-G-001B | 1010-G-001B | Alternator-LV Caterpillar G3306-GIDG_A054 | Test coolant using Nalco kit | 1 | Y | 4 | 00 |  |  | 2232756.docx
Gidgealpa Gas Satellite - Power Generation - LV Alternator Package B Unit 555 | GIDG PWR GEN 1010-G-001B | 1010-G-001B | Alternator-LV Caterpillar G3306-GIDG_A048 | Clean filter housing | 1 | Y | 4 | 00 |  |  | 2232756.docx
Gidgealpa Gas Satellite - Power Generation - LV Alternator Package B Unit 555 | GIDG PWR GEN 1010-G-001B | 1010-G-001B | Alternator-LV Caterpillar G3306-GIDG_A052 | Remove leads from coils & check for corrosion | 1 | Y | 4 | 00 |  |  | 2232756.docx
Gidgealpa Gas Satellite - Power Generation - LV Alternator Package B Unit 555 | GIDG PWR GEN 1010-G-001B | 1010-G-001B | Alternator-LV Caterpillar G3306-GIDG_A050 | Replace radiator cap | 1 | Y | 4 | 00 |  |  | 2232756.docx
Gidgealpa Gas Satellite - Power Generation - LV Alternator Package B Unit 555 | GIDG PWR GEN 1010-G-001B | 1010-G-001B | Alternator-LV Caterpillar G3306-GIDG_A012 | Inspect filter condition and clean or replace as required | 2 | M | 4 | 00 |  |  | 2231773.docx | 001
Gidgealpa Gas Satellite - Power Generation - LV Alternator Package B Unit 555 | GIDG PWR GEN 1010-G-001B | 1010-G-001B | Alternator-LV Caterpillar G3306-GIDG_A010 | Replace oil filter | 2 | M | 4 | 00 |  |  | 2231773.docx
Gidgealpa Gas Satellite - Power Generation - LV Alternator Package B Unit 555 | GIDG PWR GEN 1010-G-001B | 1010-G-001B | Alternator-LV Caterpillar G3306-GIDG_A04 | Check for abnormal noise from engine | 1 | W | 44 | 01 | 1010-G-001B 1W-44-01-001 | 1010-G-001B 1W-44-01-001 | OEC Tasks List | 001
Gidgealpa Gas Satellite - Power Generation - LV Alternator Package B Unit 555 | GIDG PWR GEN 1010-G-001B | 1010-G-001B | Alternator-LV Caterpillar G3306-GIDG_A09 | Take oil sample | 2 | M | 4 | 00 |  |  | 2231773.docx
Gidgealpa Gas Satellite - Power Generation - LV Alternator Package B Unit 555 | GIDG PWR GEN 1010-G-001B | 1010-G-001B | Alternator-LV Caterpillar G3306-GIDG_A07 | Change oil using drain valves | 2 | M | 4 | 00 |  |  | 2231773.docx | 001
Gidgealpa Gas Satellite - Power Generation - LV Alternator Package B Unit 555 | GIDG PWR GEN 1010-G-001B | 1010-G-001B | Alternator-LV Caterpillar G3306-GIDG_A08 | Re-fit plugs and close drain line valves | 2 | M | 4 | 00 |  |  | 2231773.docx | 001
Gidgealpa Gas Satellite - Power Generation - LV Alternator Package B Unit 555 | GIDG PWR GEN 1010-G-001B | 1010-G-001B | Alternator-LV Caterpillar G3306-GIDG_A049 | Replace spark plugs | 1 | Y | 4 | 00 |  |  | 2232756.docx
Gidgealpa Gas Satellite - Power Generation - LV Alternator Package B Unit 555 | GIDG PWR GEN 1010-G-001B | 1010-G-001B | Alternator-LV Caterpillar G3306-GIDG_A013 | Clean filter and housing | 2 | M | 4 | 00 |  |  | 2231773.docx
Gidgealpa Gas Satellite - Power Generation - LV Alternator Package B Unit 555 | GIDG PWR GEN 1010-G-001B | 1010-G-001B | Alternator-LV Caterpillar G3306-GIDG_A011 | Re-fill sump with new oil to correct level | 2 | M | 4 | 00 |  |  | 2231773.docx
Gidgealpa Gas Satellite - Power Generation - LV Alternator Package B Unit 555 | GIDG PWR GEN 1010-G-001B | 1010-G-001B | Alternator-LV Caterpillar G3306-GIDG_A046 | Inspect the engine fill and drain points for visible oil leaks, clean and repair as required | 1 | Y | 4 | 00 |  |  | 2232756.docx
Gidgealpa Gas Satellite - Power Generation - LV Alternator Package B Unit 555 | GIDG PWR GEN 1010-G-001B | 1010-G-001B | Alternator-LV Caterpillar G3306-GIDG_A06 | For Emergency Diesel Generator, Check diesel Fuel level | 1 | W | 44 | 01 | 1010-G-001B 1W-44-01- | 1010-G-001B 1W-44-01- | OEC Tasks List
Gidgealpa Gas Satellite - Power Generation - LV Alternator Package B Unit 555 | GIDG PWR GEN 1010-G-001B | 1010-G-001B | Alternator-LV Caterpillar G3306-GIDG_A039 | Inspect engine mounts for cracks or looseness | 6 | M | 4 | 00 |  |  | 2232574.docx
Gidgealpa Gas Satellite - Power Generation - LV Alternator Package B Unit 555 | GIDG PWR GEN 1010-G-001B | 1010-G-001B | Alternator-LV Caterpillar G3306-GIDG_A05 | For Emergency Diesel Generator, Start the set and run to check running condition | 1 | W | 44 | 01 | 1010-G-001B 1W-44-01- | 1010-G-001B 1W-44-01- | OEC Tasks List
Gidgealpa Gas Satellite - Power Generation - LV Alternator Package B Unit 555 | GIDG PWR GEN 1010-G-001B | 1010-G-001B | Alternator-LV Caterpillar G3306-GIDG_A041 | Inspect wiring | 6 | M | 4 | 00 |  |  | 2232574.docx
Gidgealpa Gas Satellite - Power Generation - LV Alternator Package B Unit 555 | GIDG PWR GEN 1010-G-001B | 1010-G-001B | Alternator-LV Caterpillar G3306-GIDG_A037 | Check wiring continuity and resistance in activated and non-activated state | 6 | M | 4 | 00 |  |  | 2232159.docx | 001
Gidgealpa Gas Satellite - Power Generation - LV Alternator Package B Unit 555 | GIDG PWR GEN 1010-G-001B | 1010-G-001B | Alternator-LV Caterpillar G3306-GIDG_A017 | Remove battery cables at battery | 2 | M | 4 | 00 |  |  | 2231773.docx | 001
Gidgealpa Gas Satellite - Power Generation - LV Alternator Package B Unit 555 | GIDG PWR GEN 1010-G-001B | 1010-G-001B | Alternator-LV Caterpillar G3306-GIDG_A035 | Check all exposed wiring for chaffing | 6 | M | 4 | 00 |  |  | 2232159.docx
Gidgealpa Gas Satellite - Power Generation - LV Alternator Package B Unit 555 | GIDG PWR GEN 1010-G-001B | 1010-G-001B | Alternator-LV Caterpillar G3306-GIDG_A018 | Clean positive and negative battery terminals and cable connectors with wire brush | 2 | M | 4 | 00 |  |  | 2231773.docx
Gidgealpa Gas Satellite - Power Generation - LV Alternator Package B Unit 555 | GIDG PWR GEN 1010-G-001B | 1010-G-001B | Alternator-LV Caterpillar G3306-GIDG_A019 | Check terminal and connector for corrosion and condition | 2 | M | 4 | 00 |  |  | 2231773.docx
Gidgealpa Gas Satellite - Power Generation - LV Alternator Package C Unit 810 | GIDG PWR GEN 1010-G-001C | 1010-G-001C | Alternator-LV Caterpillar G3306-GIDG_A020 | Ensure terminals are tight and apply battery protector | 2 | M | 4 | 00 |  |  | 2231773.docx
Gidgealpa Gas Satellite - Power Generation - LV Alternator Package C Unit 810 | GIDG PWR GEN 1010-GX-001C | 1010-GX-001C | Alternator-LV Package IE Caterpillar G3306-GIDG_A081 | Check battery terminals for corrosion | 1 | Y | 01 | 00 |  |  | 2219764.docx
Gidgealpa Gas Satellite - Power Generation - LV Alternator Package C Unit 810 | GIDG PWR GEN 1010-GX-001C | 1010-GX-001C | Alternator-LV Package IE Caterpillar G3306-GIDG_A078 | Inspect power cabling from the Alternator to the circuit breaker | 1 | Y | 01 | 00 |  |  | 2219764.docx
Gidgealpa Gas Satellite - Power Generation - LV Alternator Package C Unit 810 | GIDG PWR GEN 1010-GX-001C | 1010-GX-001C | Alternator-LV Package IE Caterpillar G3306-GIDG_A062 | Inspect external Earth connections at Alternator Main Terminal Box for signs of corrosion and check earth cable connections for tightness | 1 | Y | 01 | 00 |  |  | 2219764.docx
Gidgealpa Gas Satellite - Power Generation - LV Alternator Package C Unit 810 | GIDG PWR GEN 1010-GX-001C | 1010-GX-001C | Alternator-LV Package IE Caterpillar G3306-GIDG_A074 | Inspect the Unit Control Panel door gasket for signs of dust ingress or gaskets damage | 1 | Y | 01 | 00 |  |  | 2219764.docx
Gidgealpa Gas Satellite - Power Generation - LV Alternator Package C Unit 810 | GIDG PWR GEN 1010-GX-001C | 1010-GX-001C | Alternator-LV Package IE Caterpillar G3306-GIDG_A064 | Inspect all Alternator External Earth connections for signs of corrosion and check earth cable connections for tightness | 1 | Y | 01 | 00 |  |  | 2219764.docx
Gidgealpa Gas Satellite - Power Generation - LV Alternator Package C Unit 810 | GIDG PWR GEN 1010-GX-001C | 1010-GX-001C | Alternator-LV Package IE Caterpillar G3306-GIDG_A070 | Inspect all electronic components and potentiometers on the AVR for signs of heat discolouration | 1 | Y | 01 | 00 |  |  | 2219764.docx
Gidgealpa Gas Satellite - Power Generation - LV Alternator Package C Unit 810 | GIDG PWR GEN 1010-GX-001C | 1010-GX-001C | Alternator-LV Package IE Caterpillar G3306-GIDG_A079 | Inspect power cabling for loose or missing supports, missing cable ties or contact with sharp edges / rough surfaces | 1 | Y | 01 | 00 |  |  | 2219764.docx
Gidgealpa Gas Satellite - Power Generation - LV Alternator Package C Unit 810 | GIDG PWR GEN 1010-GX-001C | 1010-GX-001C | Alternator-LV Package IE Caterpillar G3306-GIDG_A069 | Inspect exterior condition of AVR for damaged panels or missing screws | 1 | Y | 01 | 00 |  |  | 2219764.docx
Gidgealpa Gas Satellite - Power Generation - LV Alternator Package C Unit 810 | GIDG PWR GEN 1010-GX-001C | 1010-GX-001C | Alternator-LV Package IE Caterpillar G3306-GIDG_A061 | Inspect exterior of alternator unit for damage, missing bolts, missing or loose covers, missing cable ties, or a build up of oil or dust | 1 | Y | 01 | 00 |  |  | 2219764.docx
Gidgealpa Gas Satellite - Power Generation - LV Alternator Package C Unit 810 | GIDG PWR GEN 1010-GX-001C | 1010-GX-001C | Alternator-LV Package IE Caterpillar G3306-GIDG_A065 | Inspect condition of all Unit Control Panel buttons for damage that prevents normal operation | 1 | Y | 01 | 00 |  |  | 2219764.docx
Gidgealpa Gas Satellite - Power Generation - LV Alternator Package C Unit 810 | GIDG PWR GEN 1010-GX-001C | 1010-GX-001C | Alternator-LV Package IE Caterpillar G3306-GIDG_A063 | Clean off any corrosion and repair, re-terminate or tighten connection if required | 1 | Y | 01 | 00 |  |  | 2219764.docx
Gidgealpa Gas Satellite - Power Generation - LV Alternator Package C Unit 810 | GIDG PWR GEN 1010-GX-001C | 1010-GX-001C | Alternator-LV Package IE Caterpillar G3306-GIDG_A059 | Ensure all redundant items not required in the electrical panels | 1 | Y | 01 | 00 |  |  | 2219764.docx
Gidgealpa Gas Satellite - Power Generation - LV Alternator Package C Unit 810 | GIDG PWR GEN 1010-GX-001C | 1010-GX-001C | Alternator-LV Package IE Caterpillar G3306-GIDG_A060 | Check Electrical Hazard Warning signs to ensure they are securely mounted and legible | 1 | Y | 01 | 00 |  |  | 2219764.docx
Gidgealpa Gas Satellite - Power Generation - LV Alternator Package C Unit 810 | GIDG PWR GEN 1010-GX-001C | 1010-GX-001C | Alternator-LV Package IE Caterpillar G3306-GIDG_A072 | Inspect all other terminals and circuit wiring connections on the Unit Control Panel for signs of heat discolouration | 1 | Y | 01 | 00 |  |  | 2219764.docx
Gidgealpa Gas Satellite - Power Generation - LV Alternator Package C Unit 810 | GIDG PWR GEN 1010-GX-001C | 1010-GX-001C | Alternator-LV Package IE Caterpillar G3306-GIDG_A077 | Clean off all expelled grease | 1 | Y | 01 | 00 |  |  | 2219764.docx
Gidgealpa Gas Satellite - Power Generation - LV Alternator Package C Unit 810 | GIDG PWR GEN 1010-GX-001C | 1010-GX-001C | Alternator-LV Package IE Caterpillar G3306-GIDG_A067 | Inspect terminals and circuit wiring connections on the AVR unit for signs of heat discolouration | 1 | Y | 01 | 00 |  |  | 2219764.docx
Gidgealpa Gas Satellite - Power Generation - LV Alternator Package C Unit 810 | GIDG PWR GEN 1010-GX-001C | 1010-GX-001C | Alternator-LV Package IE Caterpillar G3306-GIDG_A071 | Check the AVR heat sink cooling fins for build up of dust, clean as required | 1 | Y | 01 | 00 |  |  | 2219764.docx
Gidgealpa Gas Satellite - Power Generation - LV Alternator Package C Unit 810 | GIDG PWR GEN 1010-GX-001C | 1010-GX-001C | Alternator-LV Package IE Caterpillar G3306-GIDG_A080 | Check battery electrolyte level in each cell, top up if required with de-min water | 1 | Y | 01 | 00 |  |  | 2219764.docx
Gidgealpa Gas Satellite - Power Generation - LV Alternator Package C Unit 810 | GIDG PWR GEN 1010-GX-001C | 1010-GX-001C | Alternator-LV Package IE Caterpillar G3306-GIDG_A073 | Clean and vacuum the Unit Control Panel control cabinet, ensure all heat sink cooling fins are clean | 1 | Y | 01 | 00 |  |  | 2219764.docx
Gidgealpa Gas Satellite - Power Generation - LV Alternator Package C Unit 810 | GIDG PWR GEN 1010-GX-001C | 1010-GX-001C | Alternator-LV Package IE Caterpillar G3306-GIDG_A075 | Check the circuit breaker fixing bolts for tighness | 1 | Y | 01 | 00 |  |  | 2219764.docx
Gidgealpa Gas Satellite - Power Generation - LV Alternator Package C Unit 810 | GIDG PWR GEN 1010-GX-001C | 1010-GX-001C | Alternator-LV Package IE Caterpillar G3306-GIDG_A066 | Inspect the condition of all panel meters | 1 | Y | 01 | 00 |  |  | 2219764.docx
Gidgealpa Gas Satellite - Power Generation - LV Alternator Package C Unit 810 | GIDG PWR GEN 1010-GX-001C | 1010-GX-001C | Alternator-LV Package IE Caterpillar G3306-GIDG_A068 | Check the security of the connections by applying force to the wires | 1 | Y | 01 | 00 |  |  | 2219764.docx
Gidgealpa Gas Satellite - Power Generation - LV Alternator Package C Unit 810 | GIDG PWR GEN 1010-GX-001C | 1010-GX-001C | Alternator-LV Package IE Caterpillar G3306-GIDG_A083 | Inspect the condition of all charger panel meters and ensure they operate as expected | 1 | Y | 01 | 00 |  |  | 2219764.docx
Gidgealpa Gas Satellite - Power Generation - LV Alternator Package C Unit 810 | GIDG PWR GEN 1010-GX-001C | 1010-GX-001C | Alternator-LV Package IE Caterpillar G3306-GIDG_A082 | Check the battery charger amp meter, float voltage and boost voltage for expected values | 1 | Y | 01 | 00 |  |  | 2219764.docx
Gidgealpa Gas Satellite - Power Generation - LV Alternator Package C Unit 810 | GIDG PWR GEN 1010-GX-001C | 1010-GX-001C | Alternator-LV Package IE Caterpillar G3306-GIDG_A076 | Lubricate Alternator Bearings | 1 | Y | 01 | 00 |  |  | 2219764.docx
Gidgealpa Gas Satellite - Power Generation - LV Alternator Package C Unit 810 | GIDG PWR GEN 1010-G-001C | 1010-G-001C | Alternator-LV Caterpillar G3306-GIDG_A025 | Check radiator cores for blockage | 2 | M | 4 | 00 |  |  | 2231773.docx
Gidgealpa Gas Satellite - Power Generation - LV Alternator Package C Unit 810 | GIDG PWR GEN 1010-G-001C | 1010-G-001C | Alternator-LV Caterpillar G3306-GIDG_A033 | Inspect all coolant hoses and pipe joints for leaks | 6 | M | 4 | 00 |  |  | 2232159.docx
Gidgealpa Gas Satellite - Power Generation - LV Alternator Package C Unit 810 | GIDG PWR GEN 1010-G-001C | 1010-G-001C | Alternator-LV Caterpillar G3306-GIDG_A026 | Clean and remove any blockages | 2 | M | 4 | 00 |  |  | 2231773.docx
Gidgealpa Gas Satellite - Power Generation - LV Alternator Package C Unit 810 | GIDG PWR GEN 1010-G-001C | 1010-G-001C | Alternator-LV Caterpillar G3306-GIDG_A034 | Ensure hoses are in good condition | 6 | M | 4 | 00 |  |  | 2232159.docx
Gidgealpa Gas Satellite - Power Generation - LV Alternator Package C Unit 810 | GIDG PWR GEN 1010-G-001C | 1010-G-001C | Alternator-LV Caterpillar G3306-GIDG_A032 | Inspect air intake hoses for deterioration or cracks | 6 | M | 4 | 00 |  |  | 2232159.docx
Gidgealpa Gas Satellite - Power Generation - LV Alternator Package C Unit 810 | GIDG PWR GEN 1010-G-001C | 1010-G-001C | Alternator-LV Caterpillar G3306-GIDG_A038 | Lubricate rear alternator bearing | 6 | M | 4 | 00 |  |  | 2232159.docx
Gidgealpa Gas Satellite - Power Generation - LV Alternator Package C Unit 810 | GIDG PWR GEN 1010-G-001C | 1010-G-001C | Alternator-LV Caterpillar G3306-GIDG_A036 | Function test oil press low shutdown switch | 6 | M | 4 | 00 |  |  | 2232159.docx
Gidgealpa Gas Satellite - Power Generation - LV Alternator Package C Unit 810 | GIDG PWR GEN 1010-G-001C | 1010-G-001C | Alternator-LV Caterpillar G3306-GIDG_A056 | Replace cylinder head temp shutdown switch | 1 | Y | 01 | 00 |  |  | 2232756.docx
Gidgealpa Gas Satellite - Power Generation - LV Alternator Package C Unit 810 | GIDG PWR GEN 1010-G-001C | 1010-G-001C | Alternator-LV Caterpillar G3306-GIDG_A04 | Check for abnormal noise from engine | 1 | W | 44 | 01 | 1010-G-001C 1W-44-01- | 1010-G-001C 1W-44-01- | OEC Tasks List
Gidgealpa Gas Satellite - Power Generation - LV Alternator Package C Unit 810 | GIDG PWR GEN 1010-G-001C | 1010-G-001C | Alternator-LV Caterpillar G3306-GIDG_A046 | Inspect the engine fill and drain points for visible oil leaks, clean and repair as required | 1 | Y | 4 | 00 |  |  | 2232756.docx
Gidgealpa Gas Satellite - Power Generation - LV Alternator Package C Unit 810 | GIDG PWR GEN 1010-G-001C | 1010-G-001C | Alternator-LV Caterpillar G3306-GIDG_A06 | For Emergency Diesel Generator, Check diesel Fuel level | 1 | W | 44 | 01 | 1010-G-001C 1W-44-01- | 1010-G-001C 1W-44-01- | OEC Tasks List
Gidgealpa Gas Satellite - Power Generation - LV Alternator Package C Unit 810 | GIDG PWR GEN 1010-G-001C | 1010-G-001C | Alternator-LV Caterpillar G3306-GIDG_A039 | Inspect engine mounts for cracks or looseness | 6 | M | 4 | 00 |  |  | 2232574.docx
Gidgealpa Gas Satellite - Power Generation - LV Alternator Package C Unit 810 | GIDG PWR GEN 1010-G-001C | 1010-G-001C | Alternator-LV Caterpillar G3306-GIDG_A05 | For Emergency Diesel Generator, Start the set and run to check running condition | 1 | W | 44 | 01 | 1010-G-001C 1W-44-01- | 1010-G-001C 1W-44-01- | OEC Tasks List
Gidgealpa Gas Satellite - Power Generation - LV Alternator Package C Unit 810 | GIDG PWR GEN 1010-G-001C | 1010-G-001C | Alternator-LV Caterpillar G3306-GIDG_A02 | Check cooling system for leaks, check level and top up as required | 1 | W | 44 | 01 | 1010-G-001C 1W-44-01- | 1010-G-001C 1W-44-01- | OEC Tasks List
Gidgealpa Gas Satellite - Power Generation - LV Alternator Package C Unit 810 | GIDG PWR GEN 1010-G-001C | 1010-G-001C | Alternator-LV Caterpillar G3306-GIDG_A042 | Drain the oil from the engine | 1 | Y | 4 | 00 |  |  | 2232756.docx
Gidgealpa Gas Satellite - Power Generation - LV Alternator Package C Unit 810 | GIDG PWR GEN 1010-G-001C | 1010-G-001C | Alternator-LV Caterpillar G3306-GIDG_A043 | Remove and replace the engine oil filter | 1 | Y | 4 | 00 |  |  | 2232756.docx
Gidgealpa Gas Satellite - Power Generation - LV Alternator Package C Unit 810 | GIDG PWR GEN 1010-G-001C | 1010-G-001C | Alternator-LV Caterpillar G3306-GIDG_A045 | Fill the engine with oil | 1 | Y | 4 | 00 |  |  | 2232756.docx
Gidgealpa Gas Satellite - Power Generation - LV Alternator Package C Unit 810 | GIDG PWR GEN 1010-G-001C | 1010-G-001C | Alternator-LV Caterpillar G3306-GIDG_A044 | Replace the engine drain plugs | 1 | Y | 4 | 00 |  |  | 2232756.docx
Gidgealpa Gas Satellite - Power Generation - LV Alternator Package C Unit 810 | GIDG PWR GEN 1010-G-001C | 1010-G-001C | Alternator-LV Caterpillar G3306-GIDG_A051 | Remove and clean engine oil auto leveller | 1 | Y | 4 | 00 |  |  | 2232756.docx
Gidgealpa Gas Satellite - Power Generation - LV Alternator Package C Unit 810 | GIDG PWR GEN 1010-G-001C | 1010-G-001C | Alternator-LV Caterpillar G3306-GIDG_A01 | Check engine oil levels, check for leaks | 1 | W | 44 | 01 | 1010-G-001C 1W-44-01- | 1010-G-001C 1W-44-01- | OEC Tasks List
Gidgealpa Gas Satellite - Power Generation - LV Alternator Package C Unit 810 | GIDG PWR GEN 1010-G-001C | 1010-G-001C | Alternator-LV Caterpillar G3306-GIDG_A03 | Check air filter blockage indicators, air cooling system water flow | 1 | W | 44 | 01 | 1010-G-001C 1W-44-01- | 1010-G-001C 1W-44-01- | OEC Tasks List
Gidgealpa Gas Satellite - Power Generation - LV Alternator Package C Unit 810 | GIDG PWR GEN 1010-G-001C | 1010-G-001C | Alternator-LV Caterpillar G3306-GIDG_A024 | Check coolant level | 2 | M | 4 | 00 |  |  | 2231773.docx
Gidgealpa Gas Satellite - Power Generation - LV Alternator Package C Unit 810 | GIDG PWR GEN 1010-G-001C | 1010-G-001C | Alternator-LV Caterpillar G3306-GIDG_A027 | Adjust valve lash / tappets | 2 | M | 4 | 00 |  |  | 2231773.docx
Gidgealpa Gas Satellite - Power Generation - LV Alternator Package C Unit 810 | GIDG PWR GEN 1010-G-001C | 1010-G-001C | Alternator-LV Caterpillar G3306-GIDG_A053 | Clean and remove any corrosion buildup | 1 | Y | 4 | 00 |  |  | 2232756.docx
Gidgealpa Gas Satellite - Power Generation - LV Alternator Package C Unit 810 | GIDG PWR GEN 1010-G-001C | 1010-G-001C | Alternator-LV Caterpillar G3306-GIDG_A023 | Replace fan belt or alternator belt | 2 | M | 4 | 00 |  |  | 2231773.docx
Gidgealpa Gas Satellite - Power Generation - LV Alternator Package C Unit 810 | GIDG PWR GEN 1010-G-001C | 1010-G-001C | Alternator-LV Caterpillar G3306-GIDG_A014 | Replace air filter element and clean housing | 2 | M | 4 | 00 |  |  | 2231773.docx
Gidgealpa Gas Satellite - Power Generation - LV Alternator Package C Unit 810 | GIDG PWR GEN 1010-G-001C | 1010-G-001C | Alternator-LV Caterpillar G3306-GIDG_A030 | Clean crankcase breather | 2 | M | 4 | 00 |  |  | 2231773.docx
Gidgealpa Gas Satellite - Power Generation - LV Alternator Package C Unit 810 | GIDG PWR GEN 1010-G-001C | 1010-G-001C | Alternator-LV Caterpillar G3306-GIDG_A016 | Check the electrolyte level in the batteries and top up as required | 2 | M | 4 | 00 |  |  | 2231773.docx
Gidgealpa Gas Satellite - Power Generation - LV Alternator Package C Unit 810 | GIDG PWR GEN 1010-G-001C | 1010-G-001C | Alternator-LV Caterpillar G3306-GIDG_A040 | Ensure alignment of drive has not altered If replacements or re-tensioning | 6 | M | 4 | 00 |  |  | 2232574.docx
Gidgealpa Gas Satellite - Power Generation - LV Alternator Package C Unit 810 | GIDG PWR GEN 1010-G-001C | 1010-G-001C | Alternator-LV Caterpillar G3306-GIDG_A047 | Replace air filter element | 1 | Y | 4 | 00 |  |  | 2232756.docx
Gidgealpa Gas Satellite - Power Generation - LV Alternator Package C Unit 810 | GIDG PWR GEN 1010-G-001C | 1010-G-001C | Alternator-LV Caterpillar G3306-GIDG_A031 | Lubricate carburettor linkage | 2 | M | 4 | 00 |  |  | 2231773.docx
Gidgealpa Gas Satellite - Power Generation - LV Alternator Package C Unit 810 | GIDG PWR GEN 1010-G-001C | 1010-G-001C | Alternator-LV Caterpillar G3306-GIDG_A028 | Check and adjust intake and exhaust valve lash | 2 | M | 4 | 00 |  |  | 2231773.docx
Gidgealpa Gas Satellite - Power Generation - LV Alternator Package C Unit 810 | GIDG PWR GEN 1010-G-001C | 1010-G-001C | Alternator-LV Caterpillar G3306-GIDG_A029 | Re-fit existing rocker cover gasket and tension rocker cover | 2 | M | 4 | 00 |  |  | 2231773.docx
Gidgealpa Gas Satellite - Power Generation - LV Alternator Package C Unit 810 | GIDG PWR GEN 1010-G-001C | 1010-G-001C | Alternator-LV Caterpillar G3306-GIDG_A022 | Check fan belt condition | 2 | M | 4 | 00 |  |  | 2231773.docx
Gidgealpa Gas Satellite - Power Generation - LV Alternator Package C Unit 810 | GIDG PWR GEN 1010-G-001C | 1010-G-001C | Alternator-LV Caterpillar G3306-GIDG_A021 | Lubricate fan drive & Idler pulley | 2 | M | 4 | 00 |  |  | 2231773.docx
Gidgealpa Gas Satellite - Power Generation - LV Alternator Package C Unit 810 | GIDG PWR GEN 1010-G-001C | 1010-G-001C | Alternator-LV Caterpillar G3306-GIDG_A015 | Clean oil header tank sight glasses & breather | 2 | M | 4 | 00 |  |  | 2231773.docx
Gidgealpa Gas Satellite - Power Generation - LV Alternator Package C Unit 810 | GIDG PWR GEN 1010-G-001C | 1010-G-001C | Alternator-LV Caterpillar G3306-GIDG_A055 | Re-dose coolant if required | 1 | Y | 4 | 00 |  |  | 2232756.docx
Gidgealpa Gas Satellite - Power Generation - LV Alternator Package C Unit 810 | GIDG PWR GEN 1010-G-001C | 1010-G-001C | Alternator-LV Caterpillar G3306-GIDG_A058 | Carry Out Top End Overhaul | 3 | Y | 4 | 00 |  |  | 2256646.docx
Gidgealpa Gas Satellite - Power Generation - LV Alternator Package C Unit 810 | GIDG PWR GEN 1010-G-001C | 1010-G-001C | Alternator-LV Caterpillar G3306-GIDG_A057 | Carry out Unit Overhaul | 3 | Y | 4 | 00 |  |  | 2222484.docx
Gidgealpa Gas Satellite - Power Generation - LV Alternator Package C Unit 810 | GIDG PWR GEN 1010-G-001C | 1010-G-001C | Alternator-LV Caterpillar G3306-GIDG_A054 | Test coolant using Nalco kit | 1 | Y | 4 | 00 |  |  | 2232756.docx
Gidgealpa Gas Satellite - Power Generation - LV Alternator Package C Unit 810 | GIDG PWR GEN 1010-G-001C | 1010-G-001C | Alternator-LV Caterpillar G3306-GIDG_A048 | Clean filter housing | 1 | Y | 4 | 00 |  |  | 2232756.docx
Gidgealpa Gas Satellite - Power Generation - LV Alternator Package C Unit 810 | GIDG PWR GEN 1010-G-001C | 1010-G-001C | Alternator-LV Caterpillar G3306-GIDG_A052 | Remove leads from coils & check for corrosion | 1 | Y | 4 | 00 |  |  | 2232756.docx
Gidgealpa Gas Satellite - Power Generation - LV Alternator Package C Unit 810 | GIDG PWR GEN 1010-G-001C | 1010-G-001C | Alternator-LV Caterpillar G3306-GIDG_A050 | Replace radiator cap | 1 | Y | 4 | 00 |  |  | 2232756.docx
Gidgealpa Gas Satellite - Power Generation - LV Alternator Package C Unit 810 | GIDG PWR GEN 1010-G-001C | 1010-G-001C | Alternator-LV Caterpillar G3306-GIDG_A012 | Inspect filter condition and clean or replace as required | 2 | M | 4 | 00 |  |  | 2231773.docx
Gidgealpa Gas Satellite - Power Generation - LV Alternator Package C Unit 810 | GIDG PWR GEN 1010-G-001C | 1010-G-001C | Alternator-LV Caterpillar G3306-GIDG_A010 | Replace oil filter | 2 | M | 4 | 00 |  |  | 2231773.docx
Gidgealpa Gas Satellite - Power Generation - LV Alternator Package C Unit 810 | GIDG PWR GEN 1010-G-001C | 1010-G-001C | Alternator-LV Caterpillar G3306-GIDG_A09 | Take oil sample | 2 | M | 4 | 00 |  |  | 2231773.docx
Gidgealpa Gas Satellite - Power Generation - LV Alternator Package C Unit 810 | GIDG PWR GEN 1010-G-001C | 1010-G-001C | Alternator-LV Caterpillar G3306-GIDG_A07 | Change oil using drain valves | 2 | M | 4 | 00 |  |  | 2231773.docx
Gidgealpa Gas Satellite - Power Generation - LV Alternator Package C Unit 810 | GIDG PWR GEN 1010-G-001C | 1010-G-001C | Alternator-LV Caterpillar G3306-GIDG_A08 | Re-fit plugs and close drain line valves | 2 | M | 4 | 00 |  |  | 2231773.docx
Gidgealpa Gas Satellite - Power Generation - LV Alternator Package C Unit 810 | GIDG PWR GEN 1010-G-001C | 1010-G-001C | Alternator-LV Caterpillar G3306-GIDG_A049 | Replace spark plugs | 1 | Y | 4 | 00 |  |  | 2232756.docx
Gidgealpa Gas Satellite - Power Generation - LV Alternator Package C Unit 810 | GIDG PWR GEN 1010-G-001C | 1010-G-001C | Alternator-LV Caterpillar G3306-GIDG_A013 | Clean filter and housing | 2 | M | 4 | 00 |  |  | 2231773.docx
Gidgealpa Gas Satellite - Power Generation - LV Alternator Package C Unit 810 | GIDG PWR GEN 1010-G-001C | 1010-G-001C | Alternator-LV Caterpillar G3306-GIDG_A011 | Re-fill sump with new oil to correct level | 2 | M | 4 | 00 |  |  | 2231773.docx
Gidgealpa Gas Satellite - Power Generation - LV Alternator Package C Unit 810 | GIDG PWR GEN 1010-G-001C | 1010-G-001C | Alternator-LV Caterpillar G3306-GIDG_A041 | Inspect wiring | 6 | M | 4 | 00 |  |  | 2232574.docx
Gidgealpa Gas Satellite - Power Generation - LV Alternator Package C Unit 810 | GIDG PWR GEN 1010-G-001C | 1010-G-001C | Alternator-LV Caterpillar G3306-GIDG_A037 | Check wiring continuity and resistance in activated and non-activated state | 6 | M | 4 | 00 |  |  | 2232159.docx
Gidgealpa Gas Satellite - Power Generation - LV Alternator Package C Unit 810 | GIDG PWR GEN 1010-G-001C | 1010-G-001C | Alternator-LV Caterpillar G3306-GIDG_A017 | Remove battery cables at battery | 2 | M | 4 | 00 |  |  | 2231773.docx
Gidgealpa Gas Satellite - Power Generation - LV Alternator Package C Unit 810 | GIDG PWR GEN 1010-G-001C | 1010-G-001C | Alternator-LV Caterpillar G3306-GIDG_A035 | Check all exposed wiring for chaffing | 6 | M | 4 | 00 |  |  | 2232159.docx
Gidgealpa Gas Satellite - Power Generation - LV Alternator Package C Unit 810 | GIDG PWR GEN 1010-G-001C | 1010-G-001C | Alternator-LV Caterpillar G3306-GIDG_A018 | Clean positive and negative battery terminals and cable connectors with wire brush | 2 | M | 4 | 00 |  |  | 2231773.docx
Gidgealpa Gas Satellite - Power Generation - LV Alternator Package C Unit 810 | GIDG PWR GEN 1010-G-001C | 1010-G-001C | Alternator-LV Caterpillar G3306-GIDG_A019 | Check terminal and connector for corrosion and condition | 2 | M | 4 | 00 |  |  | 2231773.docx
Gidgealpa Gas Satellite - Power Generation - LV Alternator Package D Unit 663 | GIDG PWR GEN 1010-G-001D | 1010-G-001D | Alternator-LV Caterpillar G3306-GIDG_A020 | Ensure terminals are tight and apply battery protector | 2 | M | 4 | 00 |  |  | 2231773.docx
Gidgealpa Gas Satellite - Power Generation - LV Alternator Package D Unit 663 | GIDG PWR GEN 1010-GX-001D | 1010-GX-001D | Alternator-LV Package IE Caterpillar G3306-GIDG_A076 | Lubricate Alternator Bearings | 1 | Y | 01 | 00 |  |  | 2219764.docx
Gidgealpa Gas Satellite - Power Generation - LV Alternator Package D Unit 663 | GIDG PWR GEN 1010-GX-001D | 1010-GX-001D | Alternator-LV Package IE Caterpillar G3306-GIDG_A061 | Inspect exterior of alternator unit for damage, missing bolts, missing or loose covers, missing cable ties, or a build up of oil or dust | 1 | Y | 01 | 00 |  |  | 2219764.docx
Gidgealpa Gas Satellite - Power Generation - LV Alternator Package D Unit 663 | GIDG PWR GEN 1010-GX-001D | 1010-GX-001D | Alternator-LV Package IE Caterpillar G3306-GIDG_A072 | Inspect all other terminals and circuit wiring connections on the Unit Control Panel for signs of heat discolouration | 1 | Y | 01 | 00 |  |  | 2219764.docx
Gidgealpa Gas Satellite - Power Generation - LV Alternator Package D Unit 663 | GIDG PWR GEN 1010-GX-001D | 1010-GX-001D | Alternator-LV Package IE Caterpillar G3306-GIDG_A074 | Inspect the Unit Control Panel door gasket for signs of dust ingress or gaskets damage | 1 | Y | 01 | 00 |  |  | 2219764.docx
Gidgealpa Gas Satellite - Power Generation - LV Alternator Package D Unit 663 | GIDG PWR GEN 1010-GX-001D | 1010-GX-001D | Alternator-LV Package IE Caterpillar G3306-GIDG_A067 | Inspect terminals and circuit wiring connections on the AVR unit for signs of heat discolouration | 1 | Y | 01 | 00 |  |  | 2219764.docx
Gidgealpa Gas Satellite - Power Generation - LV Alternator Package D Unit 663 | GIDG PWR GEN 1010-GX-001D | 1010-GX-001D | Alternator-LV Package IE Caterpillar G3306-GIDG_A066 | Inspect the condition of all panel meters | 1 | Y | 01 | 00 |  |  | 2219764.docx
Gidgealpa Gas Satellite - Power Generation - LV Alternator Package D Unit 663 | GIDG PWR GEN 1010-GX-001D | 1010-GX-001D | Alternator-LV Package IE Caterpillar G3306-GIDG_A071 | Check the AVR heat sink cooling fins for build up of dust, clean as required | 1 | Y | 01 | 00 |  |  | 2219764.docx
Gidgealpa Gas Satellite - Power Generation - LV Alternator Package D Unit 663 | GIDG PWR GEN 1010-GX-001D | 1010-GX-001D | Alternator-LV Package IE Caterpillar G3306-GIDG_A073 | Clean and vacuum the Unit Control Panel control cabinet, ensure all heat sink cooling fins are clean | 1 | Y | 01 | 00 |  |  | 2219764.docx
Gidgealpa Gas Satellite - Power Generation - LV Alternator Package D Unit 663 | GIDG PWR GEN 1010-GX-001D | 1010-GX-001D | Alternator-LV Package IE Caterpillar G3306-GIDG_A068 | Check the security of the connections by applying force to the wires | 1 | Y | 01 | 00 |  |  | 2219764.docx
Gidgealpa Gas Satellite - Power Generation - LV Alternator Package D Unit 663 | GIDG PWR GEN 1010-GX-001D | 1010-GX-001D | Alternator-LV Package IE Caterpillar G3306-GIDG_A077 | Clean off all expelled grease | 1 | Y | 01 | 00 |  |  | 2219764.docx
Gidgealpa Gas Satellite - Power Generation - LV Alternator Package D Unit 663 | GIDG PWR GEN 1010-GX-001D | 1010-GX-001D | Alternator-LV Package IE Caterpillar G3306-GIDG_A075 | Check the circuit breaker fixing bolts for tighness | 1 | Y | 01 | 00 |  |  | 2219764.docx
Gidgealpa Gas Satellite - Power Generation - LV Alternator Package D Unit 663 | GIDG PWR GEN 1010-GX-001D | 1010-GX-001D | Alternator-LV Package IE Caterpillar G3306-GIDG_A080 | Check battery electrolyte level in each cell, top up if required with de-min water | 1 | Y | 01 | 00 |  |  | 2219764.docx
Gidgealpa Gas Satellite - Power Generation - LV Alternator Package D Unit 663 | GIDG PWR GEN 1010-GX-001D | 1010-GX-001D | Alternator-LV Package IE Caterpillar G3306-GIDG_A078 | Inspect power cabling from the Alternator to the circuit breaker | 1 | Y | 01 | 00 |  |  | 2219764.docx
Gidgealpa Gas Satellite - Power Generation - LV Alternator Package D Unit 663 | GIDG PWR GEN 1010-GX-001D | 1010-GX-001D | Alternator-LV Package IE Caterpillar G3306-GIDG_A081 | Check battery terminals for corrosion | 1 | Y | 01 | 00 |  |  | 2219764.docx
Gidgealpa Gas Satellite - Power Generation - LV Alternator Package D Unit 663 | GIDG PWR GEN 1010-GX-001D | 1010-GX-001D | Alternator-LV Package IE Caterpillar G3306-GIDG_A069 | Inspect exterior condition of AVR for damaged panels or missing screws | 1 | Y | 01 | 00 |  |  | 2219764.docx
Gidgealpa Gas Satellite - Power Generation - LV Alternator Package D Unit 663 | GIDG PWR GEN 1010-GX-001D | 1010-GX-001D | Alternator-LV Package IE Caterpillar G3306-GIDG_A060 | Check Electrical Hazard Warning signs to ensure they are securely mounted and legible | 1 | Y | 01 | 00 |  |  | 2219764.docx
Gidgealpa Gas Satellite - Power Generation - LV Alternator Package D Unit 663 | GIDG PWR GEN 1010-GX-001D | 1010-GX-001D | Alternator-LV Package IE Caterpillar G3306-GIDG_A065 | Inspect condition of all Unit Control Panel buttons for damage that prevents normal operation | 1 | Y | 01 | 00 |  |  | 2219764.docx
Gidgealpa Gas Satellite - Power Generation - LV Alternator Package D Unit 663 | GIDG PWR GEN 1010-GX-001D | 1010-GX-001D | Alternator-LV Package IE Caterpillar G3306-GIDG_A064 | Inspect all Alternator External Earth connections for signs of corrosion and check earth cable connections for tightness | 1 | Y | 01 | 00 |  |  | 2219764.docx
Gidgealpa Gas Satellite - Power Generation - LV Alternator Package D Unit 663 | GIDG PWR GEN 1010-GX-001D | 1010-GX-001D | Alternator-LV Package IE Caterpillar G3306-GIDG_A079 | Inspect power cabling for loose or missing supports, missing cable ties or contact with sharp edges / rough surfaces | 1 | Y | 01 | 00 |  |  | 2219764.docx
Gidgealpa Gas Satellite - Power Generation - LV Alternator Package D Unit 663 | GIDG PWR GEN 1010-GX-001D | 1010-GX-001D | Alternator-LV Package IE Caterpillar G3306-GIDG_A059 | Ensure all redundant items not required in the electrical panels | 1 | Y | 01 | 00 |  |  | 2219764.docx
Gidgealpa Gas Satellite - Power Generation - LV Alternator Package D Unit 663 | GIDG PWR GEN 1010-GX-001D | 1010-GX-001D | Alternator-LV Package IE Caterpillar G3306-GIDG_A070 | Inspect all electronic components and potentiometers on the AVR for signs of heat discolouration | 1 | Y | 01 | 00 |  |  | 2219764.docx
Gidgealpa Gas Satellite - Power Generation - LV Alternator Package D Unit 663 | GIDG PWR GEN 1010-GX-001D | 1010-GX-001D | Alternator-LV Package IE Caterpillar G3306-GIDG_A062 | Inspect external Earth connections at Alternator Main Terminal Box for signs of corrosion and check earth cable connections for tightness | 1 | Y | 01 | 00 |  |  | 2219764.docx
Gidgealpa Gas Satellite - Power Generation - LV Alternator Package D Unit 663 | GIDG PWR GEN 1010-GX-001D | 1010-GX-001D | Alternator-LV Package IE Caterpillar G3306-GIDG_A063 | Clean off any corrosion and repair, re-terminate or tighten connection if required | 1 | Y | 01 | 00 |  |  | 2219764.docx
Gidgealpa Gas Satellite - Power Generation - LV Alternator Package D Unit 663 | GIDG PWR GEN 1010-GX-001D | 1010-GX-001D | Alternator-LV Package IE Caterpillar G3306-GIDG_A082 | Check the battery charger amp meter, float voltage and boost voltage for expected values | 1 | Y | 01 | 00 |  |  | 2219764.docx
Gidgealpa Gas Satellite - Power Generation - LV Alternator Package D Unit 663 | GIDG PWR GEN 1010-GX-001D | 1010-GX-001D | Alternator-LV Package IE Caterpillar G3306-GIDG_A083 | Inspect the condition of all charger panel meters and ensure they operate as expected | 1 | Y | 01 | 00 |  |  | 2219764.docx
Gidgealpa Gas Satellite - Power Generation - LV Alternator Package D Unit 663 | GIDG PWR GEN 1010-GE-001D | 1010-GE-001D | Alternator-LV Caterpillar G3306-GIDG_A032 | Inspect air intake hoses for deterioration or cracks | 6 | M | 4 | 00 |  |  | 2232159.docx
Gidgealpa Gas Satellite - Power Generation - LV Alternator Package D Unit 663 | GIDG PWR GEN 1010-GE-001D | 1010-GE-001D | Alternator-LV Caterpillar G3306-GIDG_A033 | Inspect all coolant hoses and pipe joints for leaks | 6 | M | 4 | 00 |  |  | 2232159.docx
Gidgealpa Gas Satellite - Power Generation - LV Alternator Package D Unit 663 | GIDG PWR GEN 1010-GE-001D | 1010-GE-001D | Alternator-LV Caterpillar G3306-GIDG_A034 | Ensure hoses are in good condition | 6 | M | 4 | 00 |  |  | 2232159.docx
Gidgealpa Gas Satellite - Power Generation - LV Alternator Package D Unit 663 | GIDG PWR GEN 1010-GE-001D | 1010-GE-001D | Alternator-LV Caterpillar G3306-GIDG_A026 | Clean and remove any blockages | 2 | M | 4 | 00 |  |  | 2231773.docx
Gidgealpa Gas Satellite - Power Generation - LV Alternator Package D Unit 663 | GIDG PWR GEN 1010-GE-001D | 1010-GE-001D | Alternator-LV Caterpillar G3306-GIDG_A025 | Check radiator cores for blockage | 2 | M | 4 | 00 |  |  | 2231773.docx
Gidgealpa Gas Satellite - Power Generation - LV Alternator Package D Unit 663 | GIDG PWR GEN 1010-GE-001D | 1010-GE-001D | Alternator-LV Caterpillar G3306-GIDG_A051 | Remove and clean engine oil auto leveller | 1 | Y | 4 | 00 |  |  | 2232756.docx
Gidgealpa Gas Satellite - Power Generation - LV Alternator Package D Unit 663 | GIDG PWR GEN 1010-GE-001D | 1010-GE-001D | Alternator-LV Caterpillar G3306-GIDG_A043 | Remove and replace the engine oil filter | 1 | Y | 4 | 00 |  |  | 2232756.docx
Gidgealpa Gas Satellite - Power Generation - LV Alternator Package D Unit 663 | GIDG PWR GEN 1010-GE-001D | 1010-GE-001D | Alternator-LV Caterpillar G3306-GIDG_A044 | Replace the engine drain plugs | 1 | Y | 4 | 00 |  |  | 2232756.docx
Gidgealpa Gas Satellite - Power Generation - LV Alternator Package D Unit 663 | GIDG PWR GEN 1010-GE-001D | 1010-GE-001D | Alternator-LV Caterpillar G3306-GIDG_A042 | Drain the oil from the engine | 1 | Y | 4 | 00 |  |  | 2232756.docx
Gidgealpa Gas Satellite - Power Generation - LV Alternator Package D Unit 663 | GIDG PWR GEN 1010-GE-001D | 1010-GE-001D | Alternator-LV Caterpillar G3306-GIDG_A02 | Check cooling system for leaks, check level and top up as required | 1 | W | 44 | 01 | 1010-GE-001D 1W-44-01- | 1010-GE-001D 1W-44-01- | OEC Tasks List
Gidgealpa Gas Satellite - Power Generation - LV Alternator Package D Unit 663 | GIDG PWR GEN 1010-GE-001D | 1010-GE-001D | Alternator-LV Caterpillar G3306-GIDG_A01 | Check engine oil levels, check for leaks | 1 | W | 44 | 01 | 1010-GE-001D 1W-44-01- | 1010-GE-001D 1W-44-01- | OEC Tasks List
Gidgealpa Gas Satellite - Power Generation - LV Alternator Package D Unit 663 | GIDG PWR GEN 1010-GE-001D | 1010-GE-001D | Alternator-LV Caterpillar G3306-GIDG_A045 | Fill the engine with oil | 1 | Y | 4 | 00 |  |  | 2232756.docx
Gidgealpa Gas Satellite - Power Generation - LV Alternator Package D Unit 663 | GIDG PWR GEN 1010-GE-001D | 1010-GE-001D | Alternator-LV Caterpillar G3306-GIDG_A019 | Check terminal and connector for corrosion and condition | 2 | M | 4 | 00 |  |  | 2231773.docx
Gidgealpa Gas Satellite - Power Generation - LV Alternator Package D Unit 663 | GIDG PWR GEN 1010-GE-001D | 1010-GE-001D | Alternator-LV Caterpillar G3306-GIDG_A018 | Clean positive and negative battery terminals and cable connectors with wire brush | 2 | M | 4 | 00 |  |  | 2231773.docx
Gidgealpa Gas Satellite - Power Generation - LV Alternator Package D Unit 663 | GIDG PWR GEN 1010-GE-001D | 1010-GE-001D | Alternator-LV Caterpillar G3306-GIDG_A020 | Ensure terminals are tight and apply battery protector | 2 | M | 4 | 00 |  |  | 2231773.docx
Gidgealpa Gas Satellite - Power Generation - LV Alternator Package D Unit 663 | GIDG PWR GEN 1010-GE-001D | 1010-GE-001D | Alternator-LV Caterpillar G3306-GIDG_A037 | Check wiring continuity and resistance in activated and non-activated state | 6 | M | 4 | 00 |  |  | 2232159.docx
Gidgealpa Gas Satellite - Power Generation - LV Alternator Package D Unit 663 | GIDG PWR GEN 1010-GE-001D | 1010-GE-001D | Alternator-LV Caterpillar G3306-GIDG_A035 | Check all exposed wiring for chaffing | 6 | M | 4 | 00 |  |  | 2232159.docx
Gidgealpa Gas Satellite - Power Generation - LV Alternator Package D Unit 663 | GIDG PWR GEN 1010-GE-001D | 1010-GE-001D | Alternator-LV Caterpillar G3306-GIDG_A017 | Remove battery cables at battery | 2 | M | 4 | 00 |  |  | 2231773.docx
Gidgealpa Gas Satellite - Power Generation - LV Alternator Package D Unit 663 | GIDG PWR GEN 1010-GE-001D | 1010-GE-001D | Alternator-LV Caterpillar G3306-GIDG_A041 | Inspect wiring | 6 | M | 4 | 00 |  |  | 2232574.docx
Gidgealpa Gas Satellite - Power Generation - LV Alternator Package D Unit 663 | GIDG PWR GEN 1010-GE-001D | 1010-GE-001D | Alternator-LV Caterpillar G3306-GIDG_A010 | Replace oil filter | 2 | M | 4 | 00 |  |  | 2231773.docx
Gidgealpa Gas Satellite - Power Generation - LV Alternator Package D Unit 663 | GIDG PWR GEN 1010-GE-001D | 1010-GE-001D | Alternator-LV Caterpillar G3306-GIDG_A055 | Re-dose coolant if required | 1 | Y | 4 | 00 |  |  | 2232756.docx
Gidgealpa Gas Satellite - Power Generation - LV Alternator Package D Unit 663 | GIDG PWR GEN 1010-GE-001D | 1010-GE-001D | Alternator-LV Caterpillar G3306-GIDG_A07 | Change oil using drain valves | 2 | M | 4 | 00 |  |  | 2231773.docx
Gidgealpa Gas Satellite - Power Generation - LV Alternator Package D Unit 663 | GIDG PWR GEN 1010-GE-001D | 1010-GE-001D | Alternator-LV Caterpillar G3306-GIDG_A012 | Inspect filter condition and clean or replace as required | 2 | M | 4 | 00 |  |  | 2231773.docx
Gidgealpa Gas Satellite - Power Generation - LV Alternator Package D Unit 663 | GIDG PWR GEN 1010-GE-001D | 1010-GE-001D | Alternator-LV Caterpillar G3306-GIDG_A027 | Adjust valve lash / tappets | 2 | M | 4 | 00 |  |  | 2231773.docx
Gidgealpa Gas Satellite - Power Generation - LV Alternator Package D Unit 663 | GIDG PWR GEN 1010-GE-001D | 1010-GE-001D | Alternator-LV Caterpillar G3306-GIDG_A03 | Check air filter blockage indicators, air cooling system water flow | 1 | W | 44 | 01 | 1010-GE-001D 1W-44-01- | 1010-GE-001D 1W-44-01- | OEC Tasks List
Gidgealpa Gas Satellite - Power Generation - LV Alternator Package D Unit 663 | GIDG PWR GEN 1010-GE-001D | 1010-GE-001D | Alternator-LV Caterpillar G3306-GIDG_A053 | Clean and remove any corrosion buildup | 1 | Y | 4 | 00 |  |  | 2232756.docx
Gidgealpa Gas Satellite - Power Generation - LV Alternator Package D Unit 663 | GIDG PWR GEN 1010-GE-001D | 1010-GE-001D | Alternator-LV Caterpillar G3306-GIDG_A052 | Remove leads from coils & check for corrosion | 1 | Y | 4 | 00 |  |  | 2232756.docx
Gidgealpa Gas Satellite - Power Generation - LV Alternator Package D Unit 663 | GIDG PWR GEN 1010-GE-001D | 1010-GE-001D | Alternator-LV Caterpillar G3306-GIDG_A011 | Re-fill sump with new oil to correct level | 2 | M | 4 | 00 |  |  | 2231773.docx
Gidgealpa Gas Satellite - Power Generation - LV Alternator Package D Unit 663 | GIDG PWR GEN 1010-GE-001D | 1010-GE-001D | Alternator-LV Caterpillar G3306-GIDG_A048 | Clean filter housing | 1 | Y | 4 | 00 |  |  | 2232756.docx
Gidgealpa Gas Satellite - Power Generation - LV Alternator Package D Unit 663 | GIDG PWR GEN 1010-GE-001D | 1010-GE-001D | Alternator-LV Caterpillar G3306-GIDG_A08 | Re-fit plugs and close drain line valves | 2 | M | 4 | 00 |  |  | 2231773.docx
Gidgealpa Gas Satellite - Power Generation - LV Alternator Package D Unit 663 | GIDG PWR GEN 1010-GE-001D | 1010-GE-001D | Alternator-LV Caterpillar G3306-GIDG_A049 | Replace spark plugs | 1 | Y | 4 | 00 |  |  | 2232756.docx
Gidgealpa Gas Satellite - Power Generation - LV Alternator Package D Unit 663 | GIDG PWR GEN 1010-GE-001D | 1010-GE-001D | Alternator-LV Caterpillar G3306-GIDG_A054 | Test coolant using Nalco kit | 1 | Y | 4 | 00 |  |  | 2232756.docx
Gidgealpa Gas Satellite - Power Generation - LV Alternator Package D Unit 663 | GIDG PWR GEN 1010-GE-001D | 1010-GE-001D | Alternator-LV Caterpillar G3306-GIDG_A050 | Replace radiator cap | 1 | Y | 4 | 00 |  |  | 2232756.docx
Gidgealpa Gas Satellite - Power Generation - LV Alternator Package D Unit 663 | GIDG PWR GEN 1010-GE-001D | 1010-GE-001D | Alternator-LV Caterpillar G3306-GIDG_A09 | Take oil sample | 2 | M | 4 | 00 |  |  | 2231773.docx
Gidgealpa Gas Satellite - Power Generation - LV Alternator Package D Unit 663 | GIDG PWR GEN 1010-GE-001D | 1010-GE-001D | Alternator-LV Caterpillar G3306-GIDG_A058 | Carry Out Top End Overhaul | 3 | Y | 4 | 00 |  |  | 2256646.docx
Gidgealpa Gas Satellite - Power Generation - LV Alternator Package D Unit 663 | GIDG PWR GEN 1010-GE-001D | 1010-GE-001D | Alternator-LV Caterpillar G3306-GIDG_A013 | Clean filter and housing | 2 | M | 4 | 00 |  |  | 2231773.docx
Gidgealpa Gas Satellite - Power Generation - LV Alternator Package D Unit 663 | GIDG PWR GEN 1010-GE-001D | 1010-GE-001D | Alternator-LV Caterpillar G3306-GIDG_A057 | Carry out Unit Overhaul | 3 | Y | 4 | 00 |  |  | 2222484.docx
Gidgealpa Gas Satellite - Power Generation - LV Alternator Package D Unit 663 | GIDG PWR GEN 1010-GE-001D | 1010-GE-001D | Alternator-LV Caterpillar G3306-GIDG_A024 | Check coolant level | 2 | M | 4 | 00 |  |  | 2231773.docx
Gidgealpa Gas Satellite - Power Generation - LV Alternator Package D Unit 663 | GIDG PWR GEN 1010-GE-001D | 1010-GE-001D | Alternator-LV Caterpillar G3306-GIDG_A016 | Check the electrolyte level in the batteries and top up as required | 2 | M | 4 | 00 |  |  | 2231773.docx
Gidgealpa Gas Satellite - Power Generation - LV Alternator Package D Unit 663 | GIDG PWR GEN 1010-GE-001D | 1010-GE-001D | Alternator-LV Caterpillar G3306-GIDG_A023 | Replace fan belt or alternator belt | 2 | M | 4 | 00 |  |  | 2231773.docx
Gidgealpa Gas Satellite - Power Generation - LV Alternator Package D Unit 663 | GIDG PWR GEN 1010-GE-001D | 1010-GE-001D | Alternator-LV Caterpillar G3306-GIDG_A022 | Check fan belt condition | 2 | M | 4 | 00 |  |  | 2231773.docx
Gidgealpa Gas Satellite - Power Generation - LV Alternator Package D Unit 663 | GIDG PWR GEN 1010-GE-001D | 1010-GE-001D | Alternator-LV Caterpillar G3306-GIDG_A030 | Clean crankcase breather | 2 | M | 4 | 00 |  |  | 2231773.docx
Gidgealpa Gas Satellite - Power Generation - LV Alternator Package D Unit 663 | GIDG PWR GEN 1010-GE-001D | 1010-GE-001D | Alternator-LV Caterpillar G3306-GIDG_A014 | Replace air filter element and clean housing | 2 | M | 4 | 00 |  |  | 2231773.docx
Gidgealpa Gas Satellite - Power Generation - LV Alternator Package D Unit 663 | GIDG PWR GEN 1010-GE-001D | 1010-GE-001D | Alternator-LV Caterpillar G3306-GIDG_A028 | Check and adjust intake and exhaust valve lash | 2 | M | 4 | 00 |  |  | 2231773.docx
Gidgealpa Gas Satellite - Power Generation - LV Alternator Package D Unit 663 | GIDG PWR GEN 1010-GE-001D | 1010-GE-001D | Alternator-LV Caterpillar G3306-GIDG_A040 | Ensure alignment of drive has not altered If replacements or re-tensioning | 6 | M | 4 | 00 |  |  | 2232574.docx
Gidgealpa Gas Satellite - Power Generation - LV Alternator Package D Unit 663 | GIDG PWR GEN 1010-GE-001D | 1010-GE-001D | Alternator-LV Caterpillar G3306-GIDG_A031 | Lubricate carburettor linkage | 2 | M | 4 | 00 |  |  | 2231773.docx
Gidgealpa Gas Satellite - Power Generation - LV Alternator Package D Unit 663 | GIDG PWR GEN 1010-GE-001D | 1010-GE-001D | Alternator-LV Caterpillar G3306-GIDG_A015 | Clean oil header tank sight glasses & breather | 2 | M | 4 | 00 |  |  | 2231773.docx
Gidgealpa Gas Satellite - Power Generation - LV Alternator Package D Unit 663 | GIDG PWR GEN 1010-GE-001D | 1010-GE-001D | Alternator-LV Caterpillar G3306-GIDG_A029 | Re-fit existing rocker cover gasket and tension rocker cover | 2 | M | 4 | 00 |  |  | 2231773.docx
Gidgealpa Gas Satellite - Power Generation - LV Alternator Package D Unit 663 | GIDG PWR GEN 1010-GE-001D | 1010-GE-001D | Alternator-LV Caterpillar G3306-GIDG_A047 | Replace air filter element | 1 | Y | 4 | 00 |  |  | 2232756.docx
Gidgealpa Gas Satellite - Power Generation - LV Alternator Package D Unit 663 | GIDG PWR GEN 1010-GE-001D | 1010-GE-001D | Alternator-LV Caterpillar G3306-GIDG_A021 | Lubricate fan drive & Idler pulley | 2 | M | 4 | 00 |  |  | 2231773.docx
Gidgealpa Gas Satellite - Power Generation - LV Alternator Package D Unit 663 | GIDG PWR GEN 1010-GE-001D | 1010-GE-001D | Alternator-LV Caterpillar G3306-GIDG_A038 | Lubricate rear alternator bearing | 6 | M | 4 | 00 |  |  | 2232159.docx
Gidgealpa Gas Satellite - Power Generation - LV Alternator Package D Unit 663 | GIDG PWR GEN 1010-GE-001D | 1010-GE-001D | Alternator-LV Caterpillar G3306-GIDG_A06 | For Emergency Diesel Generator, Check diesel Fuel level | 1 | W | 44 | 01 | 1010-GE-001D 1W-44-01- | 1010-GE-001D 1W-44-01- | OEC Tasks List
Gidgealpa Gas Satellite - Power Generation - LV Alternator Package D Unit 663 | GIDG PWR GEN 1010-GE-001D | 1010-GE-001D | Alternator-LV Caterpillar G3306-GIDG_A046 | Inspect the engine fill and drain points for visible oil leaks, clean and repair as required | 1 | Y | 4 | 00 |  |  | 2232756.docx
Gidgealpa Gas Satellite - Power Generation - LV Alternator Package D Unit 663 | GIDG PWR GEN 1010-GE-001D | 1010-GE-001D | Alternator-LV Caterpillar G3306-GIDG_A05 | For Emergency Diesel Generator, Start the set and run to check running condition | 1 | W | 44 | 01 | 1010-GE-001D 1W-44-01- | 1010-GE-001D 1W-44-01- | OEC Tasks List
Gidgealpa Gas Satellite - Power Generation - LV Alternator Package D Unit 663 | GIDG PWR GEN 1010-GE-001D | 1010-GE-001D | Alternator-LV Caterpillar G3306-GIDG_A04 | Check for abnormal noise from engine | 1 | W | 44 | 01 | 1010-GE-001D 1W-44-01- | 1010-GE-001D 1W-44-01- | OEC Tasks List
Gidgealpa Gas Satellite - Power Generation - LV Alternator Package D Unit 663 | GIDG PWR GEN 1010-GE-001D | 1010-GE-001D | Alternator-LV Caterpillar G3306-GIDG_A039 | Inspect engine mounts for cracks or looseness | 6 | M | 4 | 00 |  |  | 2232574.docx
Gidgealpa Gas Satellite - Power Generation - LV Alternator Package D Unit 663 | GIDG PWR GEN 1010-GE-001D | 1010-GE-001D | Alternator-LV Caterpillar G3306-GIDG_A056 | Replace cylinder head temp shutdown switch | 1 | Y | 01 | 00 |  |  | 2232756.docx
Gidgealpa Gas Satellite - Power Generation - LV Alternator Package D Unit 663 | GIDG PWR GEN 1010-GE-001D | 1010-GE-001D | Alternator-LV Caterpillar G3306-GIDG_A036 | Function test oil press low shutdown switch | 6 | M | 4 | 00 |  |  | 2232159.docx
Gidgealpa Gas Satellite - Power Generation - LV Alternator Package D Unit 663 | GIDG PWR GEN 1010-G-001D | 1010-G-001D | Alternator-LV Caterpillar G3306-GIDG_A025 | Check radiator cores for blockage | 2 | M | 4 | 00 |  |  | 2231773.docx
Gidgealpa Gas Satellite - Power Generation - LV Alternator Package D Unit 663 | GIDG PWR GEN 1010-G-001D | 1010-G-001D | Alternator-LV Caterpillar G3306-GIDG_A033 | Inspect all coolant hoses and pipe joints for leaks | 6 | M | 4 | 00 |  |  | 2232159.docx
Gidgealpa Gas Satellite - Power Generation - LV Alternator Package D Unit 663 | GIDG PWR GEN 1010-G-001D | 1010-G-001D | Alternator-LV Caterpillar G3306-GIDG_A026 | Clean and remove any blockages | 2 | M | 4 | 00 |  |  | 2231773.docx
Gidgealpa Gas Satellite - Power Generation - LV Alternator Package D Unit 663 | GIDG PWR GEN 1010-G-001D | 1010-G-001D | Alternator-LV Caterpillar G3306-GIDG_A034 | Ensure hoses are in good condition | 6 | M | 4 | 00 |  |  | 2232159.docx
Gidgealpa Gas Satellite - Power Generation - LV Alternator Package D Unit 663 | GIDG PWR GEN 1010-G-001D | 1010-G-001D | Alternator-LV Caterpillar G3306-GIDG_A032 | Inspect air intake hoses for deterioration or cracks | 6 | M | 4 | 00 |  |  | 2232159.docx
Gidgealpa Gas Satellite - Power Generation - LV Alternator Package D Unit 663 | GIDG PWR GEN 1010-G-001D | 1010-G-001D | Alternator-LV Caterpillar G3306-GIDG_A038 | Lubricate rear alternator bearing | 6 | M | 4 | 00 |  |  | 2232159.docx
Gidgealpa Gas Satellite - Power Generation - LV Alternator Package D Unit 663 | GIDG PWR GEN 1010-G-001D | 1010-G-001D | Alternator-LV Caterpillar G3306-GIDG_A036 | Function test oil press low shutdown switch | 6 | M | 4 | 00 |  |  | 2232159.docx
Gidgealpa Gas Satellite - Power Generation - LV Alternator Package D Unit 663 | GIDG PWR GEN 1010-G-001D | 1010-G-001D | Alternator-LV Caterpillar G3306-GIDG_A056 | Replace cylinder head temp shutdown switch | 1 | Y | 01 | 00 |  |  | 2232756.docx
Gidgealpa Gas Satellite - Power Generation - LV Alternator Package D Unit 663 | GIDG PWR GEN 1010-G-001D | 1010-G-001D | Alternator-LV Caterpillar G3306-GIDG_A04 | Check for abnormal noise from engine | 1 | W | 44 | 01 | 1010-G-001D 1W-44-01- | 1010-G-001D 1W-44-01- | OEC Tasks List
Gidgealpa Gas Satellite - Power Generation - LV Alternator Package D Unit 663 | GIDG PWR GEN 1010-G-001D | 1010-G-001D | Alternator-LV Caterpillar G3306-GIDG_A046 | Inspect the engine fill and drain points for visible oil leaks, clean and repair as required | 1 | Y | 4 | 00 |  |  | 2232756.docx
Gidgealpa Gas Satellite - Power Generation - LV Alternator Package D Unit 663 | GIDG PWR GEN 1010-G-001D | 1010-G-001D | Alternator-LV Caterpillar G3306-GIDG_A06 | For Emergency Diesel Generator, Check diesel Fuel level | 1 | W | 44 | 01 | 1010-G-001D 1W-44-01- | 1010-G-001D 1W-44-01- | OEC Tasks List
Gidgealpa Gas Satellite - Power Generation - LV Alternator Package D Unit 663 | GIDG PWR GEN 1010-G-001D | 1010-G-001D | Alternator-LV Caterpillar G3306-GIDG_A039 | Inspect engine mounts for cracks or looseness | 6 | M | 4 | 00 |  |  | 2232574.docx
Gidgealpa Gas Satellite - Power Generation - LV Alternator Package D Unit 663 | GIDG PWR GEN 1010-G-001D | 1010-G-001D | Alternator-LV Caterpillar G3306-GIDG_A05 | For Emergency Diesel Generator, Start the set and run to check running condition | 1 | W | 44 | 01 | 1010-G-001D 1W-44-01- | 1010-G-001D 1W-44-01- | OEC Tasks List
Gidgealpa Gas Satellite - Power Generation - LV Alternator Package D Unit 663 | GIDG PWR GEN 1010-G-001D | 1010-G-001D | Alternator-LV Caterpillar G3306-GIDG_A03 | Check air filter blockage indicators, air cooling system water flow | 1 | W | 44 | 01 | 1010-G-001D 1W-44-01- | 1010-G-001D 1W-44-01- | OEC Tasks List
Gidgealpa Gas Satellite - Power Generation - LV Alternator Package D Unit 663 | GIDG PWR GEN 1010-G-001D | 1010-G-001D | Alternator-LV Caterpillar G3306-GIDG_A024 | Check coolant level | 2 | M | 4 | 00 |  |  | 2231773.docx
Gidgealpa Gas Satellite - Power Generation - LV Alternator Package D Unit 663 | GIDG PWR GEN 1010-G-001D | 1010-G-001D | Alternator-LV Caterpillar G3306-GIDG_A027 | Adjust valve lash / tappets | 2 | M | 4 | 00 |  |  | 2231773.docx
Gidgealpa Gas Satellite - Power Generation - LV Alternator Package D Unit 663 | GIDG PWR GEN 1010-G-001D | 1010-G-001D | Alternator-LV Caterpillar G3306-GIDG_A053 | Clean and remove any corrosion buildup | 1 | Y | 4 | 00 |  |  | 2232756.docx
Gidgealpa Gas Satellite - Power Generation - LV Alternator Package D Unit 663 | GIDG PWR GEN 1010-G-001D | 1010-G-001D | Alternator-LV Caterpillar G3306-GIDG_A023 | Replace fan belt or alternator belt | 2 | M | 4 | 00 |  |  | 2231773.docx
Gidgealpa Gas Satellite - Power Generation - LV Alternator Package D Unit 663 | GIDG PWR GEN 1010-G-001D | 1010-G-001D | Alternator-LV Caterpillar G3306-GIDG_A014 | Replace air filter element and clean housing | 2 | M | 4 | 00 |  |  | 2231773.docx
Gidgealpa Gas Satellite - Power Generation - LV Alternator Package D Unit 663 | GIDG PWR GEN 1010-G-001D | 1010-G-001D | Alternator-LV Caterpillar G3306-GIDG_A030 | Clean crankcase breather | 2 | M | 4 | 00 |  |  | 2231773.docx
Gidgealpa Gas Satellite - Power Generation - LV Alternator Package D Unit 663 | GIDG PWR GEN 1010-G-001D | 1010-G-001D | Alternator-LV Caterpillar G3306-GIDG_A016 | Check the electrolyte level in the batteries and top up as required | 2 | M | 4 | 00 |  |  | 2231773.docx
Gidgealpa Gas Satellite - Power Generation - LV Alternator Package D Unit 663 | GIDG PWR GEN 1010-G-001D | 1010-G-001D | Alternator-LV Caterpillar G3306-GIDG_A040 | Ensure alignment of drive has not altered If replacements or re-tensioning | 6 | M | 4 | 00 |  |  | 2232574.docx
Gidgealpa Gas Satellite - Power Generation - LV Alternator Package D Unit 663 | GIDG PWR GEN 1010-G-001D | 1010-G-001D | Alternator-LV Caterpillar G3306-GIDG_A047 | Replace air filter element | 1 | Y | 4 | 00 |  |  | 2232756.docx
Gidgealpa Gas Satellite - Power Generation - LV Alternator Package D Unit 663 | GIDG PWR GEN 1010-G-001D | 1010-G-001D | Alternator-LV Caterpillar G3306-GIDG_A031 | Lubricate carburettor linkage | 2 | M | 4 | 00 |  |  | 2231773.docx
Gidgealpa Gas Satellite - Power Generation - LV Alternator Package D Unit 663 | GIDG PWR GEN 1010-G-001D | 1010-G-001D | Alternator-LV Caterpillar G3306-GIDG_A028 | Check and adjust intake and exhaust valve lash | 2 | M | 4 | 00 |  |  | 2231773.docx
Gidgealpa Gas Satellite - Power Generation - LV Alternator Package D Unit 663 | GIDG PWR GEN 1010-G-001D | 1010-G-001D | Alternator-LV Caterpillar G3306-GIDG_A029 | Re-fit existing rocker cover gasket and tension rocker cover | 2 | M | 4 | 00 |  |  | 2231773.docx
Gidgealpa Gas Satellite - Power Generation - LV Alternator Package D Unit 663 | GIDG PWR GEN 1010-G-001D | 1010-G-001D | Alternator-LV Caterpillar G3306-GIDG_A022 | Check fan belt condition | 2 | M | 4 | 00 |  |  | 2231773.docx
Gidgealpa Gas Satellite - Power Generation - LV Alternator Package D Unit 663 | GIDG PWR GEN 1010-G-001D | 1010-G-001D | Alternator-LV Caterpillar G3306-GIDG_A021 | Lubricate fan drive & Idler pulley | 2 | M | 4 | 00 |  |  | 2231773.docx
Gidgealpa Gas Satellite - Power Generation - LV Alternator Package D Unit 663 | GIDG PWR GEN 1010-G-001D | 1010-G-001D | Alternator-LV Caterpillar G3306-GIDG_A015 | Clean oil header tank sight glasses & breather | 2 | M | 4 | 00 |  |  | 2231773.docx
Gidgealpa Gas Satellite - Power Generation - LV Alternator Package D Unit 663 | GIDG PWR GEN 1010-G-001D | 1010-G-001D | Alternator-LV Caterpillar G3306-GIDG_A055 | Re-dose coolant if required | 1 | Y | 4 | 00 |  |  | 2232756.docx
Gidgealpa Gas Satellite - Power Generation - LV Alternator Package D Unit 663 | GIDG PWR GEN 1010-G-001D | 1010-G-001D | Alternator-LV Caterpillar G3306-GIDG_A058 | Carry Out Top End Overhaul | 3 | Y | 4 | 00 |  |  | 2256646.docx
Gidgealpa Gas Satellite - Power Generation - LV Alternator Package D Unit 663 | GIDG PWR GEN 1010-G-001D | 1010-G-001D | Alternator-LV Caterpillar G3306-GIDG_A057 | Carry out Unit Overhaul | 3 | Y | 4 | 00 |  |  | 2222484.docx
Gidgealpa Gas Satellite - Power Generation - LV Alternator Package D Unit 663 | GIDG PWR GEN 1010-G-001D | 1010-G-001D | Alternator-LV Caterpillar G3306-GIDG_A054 | Test coolant using Nalco kit | 1 | Y | 4 | 00 |  |  | 2232756.docx
Gidgealpa Gas Satellite - Power Generation - LV Alternator Package D Unit 663 | GIDG PWR GEN 1010-G-001D | 1010-G-001D | Alternator-LV Caterpillar G3306-GIDG_A048 | Clean filter housing | 1 | Y | 4 | 00 |  |  | 2232756.docx
Gidgealpa Gas Satellite - Power Generation - LV Alternator Package D Unit 663 | GIDG PWR GEN 1010-G-001D | 1010-G-001D | Alternator-LV Caterpillar G3306-GIDG_A052 | Remove leads from coils & check for corrosion | 1 | Y | 4 | 00 |  |  | 2232756.docx
Gidgealpa Gas Satellite - Power Generation - LV Alternator Package D Unit 663 | GIDG PWR GEN 1010-G-001D | 1010-G-001D | Alternator-LV Caterpillar G3306-GIDG_A050 | Replace radiator cap | 1 | Y | 4 | 00 |  |  | 2232756.docx
Gidgealpa Gas Satellite - Power Generation - LV Alternator Package D Unit 663 | GIDG PWR GEN 1010-G-001D | 1010-G-001D | Alternator-LV Caterpillar G3306-GIDG_A012 | Inspect filter condition and clean or replace as required | 2 | M | 4 | 00 |  |  | 2231773.docx
Gidgealpa Gas Satellite - Power Generation - LV Alternator Package D Unit 663 | GIDG PWR GEN 1010-G-001D | 1010-G-001D | Alternator-LV Caterpillar G3306-GIDG_A010 | Replace oil filter | 2 | M | 4 | 00 |  |  | 2231773.docx
Gidgealpa Gas Satellite - Power Generation - LV Alternator Package D Unit 663 | GIDG PWR GEN 1010-G-001D | 1010-G-001D | Alternator-LV Caterpillar G3306-GIDG_A09 | Take oil sample | 2 | M | 4 | 00 |  |  | 2231773.docx
Gidgealpa Gas Satellite - Power Generation - LV Alternator Package D Unit 663 | GIDG PWR GEN 1010-G-001D | 1010-G-001D | Alternator-LV Caterpillar G3306-GIDG_A07 | Change oil using drain valves | 2 | M | 4 | 00 |  |  | 2231773.docx
Gidgealpa Gas Satellite - Power Generation - LV Alternator Package D Unit 663 | GIDG PWR GEN 1010-G-001D | 1010-G-001D | Alternator-LV Caterpillar G3306-GIDG_A08 | Re-fit plugs and close drain line valves | 2 | M | 4 | 00 |  |  | 2231773.docx
Gidgealpa Gas Satellite - Power Generation - LV Alternator Package D Unit 663 | GIDG PWR GEN 1010-G-001D | 1010-G-001D | Alternator-LV Caterpillar G3306-GIDG_A049 | Replace spark plugs | 1 | Y | 4 | 00 |  |  | 2232756.docx
Gidgealpa Gas Satellite - Power Generation - LV Alternator Package D Unit 663 | GIDG PWR GEN 1010-G-001D | 1010-G-001D | Alternator-LV Caterpillar G3306-GIDG_A013 | Clean filter and housing | 2 | M | 4 | 00 |  |  | 2231773.docx
Gidgealpa Gas Satellite - Power Generation - LV Alternator Package D Unit 663 | GIDG PWR GEN 1010-G-001D | 1010-G-001D | Alternator-LV Caterpillar G3306-GIDG_A011 | Re-fill sump with new oil to correct level | 2 | M | 4 | 00 |  |  | 2231773.docx
Gidgealpa Gas Satellite - Power Generation - LV Alternator Package D Unit 663 | GIDG PWR GEN 1010-G-001D | 1010-G-001D | Alternator-LV Caterpillar G3306-GIDG_A041 | Inspect wiring | 6 | M | 4 | 00 |  |  | 2232574.docx
Gidgealpa Gas Satellite - Power Generation - LV Alternator Package D Unit 663 | GIDG PWR GEN 1010-G-001D | 1010-G-001D | Alternator-LV Caterpillar G3306-GIDG_A037 | Check wiring continuity and resistance in activated and non-activated state | 6 | M | 4 | 00 |  |  | 2232159.docx
Gidgealpa Gas Satellite - Power Generation - LV Alternator Package D Unit 663 | GIDG PWR GEN 1010-G-001D | 1010-G-001D | Alternator-LV Caterpillar G3306-GIDG_A017 | Remove battery cables at battery | 2 | M | 4 | 00 |  |  | 2231773.docx
Gidgealpa Gas Satellite - Power Generation - LV Alternator Package D Unit 663 | GIDG PWR GEN 1010-G-001D | 1010-G-001D | Alternator-LV Caterpillar G3306-GIDG_A035 | Check all exposed wiring for chaffing | 6 | M | 4 | 00 |  |  | 2232159.docx
Gidgealpa Gas Satellite - Power Generation - LV Alternator Package D Unit 663 | GIDG PWR GEN 1010-G-001D | 1010-G-001D | Alternator-LV Caterpillar G3306-GIDG_A02 | Check cooling system for leaks, check level and top up as required | 1 | W | 44 | 01 | 1010-G-001D 1W-44-01- | 1010-G-001D 1W-44-01- | OEC Tasks List
Gidgealpa Gas Satellite - Power Generation - LV Alternator Package D Unit 663 | GIDG PWR GEN 1010-G-001D | 1010-G-001D | Alternator-LV Caterpillar G3306-GIDG_A042 | Drain the oil from the engine | 1 | Y | 4 | 00 |  |  | 2232756.docx
Gidgealpa Gas Satellite - Power Generation - LV Alternator Package D Unit 663 | GIDG PWR GEN 1010-G-001D | 1010-G-001D | Alternator-LV Caterpillar G3306-GIDG_A043 | Remove and replace the engine oil filter | 1 | Y | 4 | 00 |  |  | 2232756.docx
Gidgealpa Gas Satellite - Power Generation - LV Alternator Package D Unit 663 | GIDG PWR GEN 1010-G-001D | 1010-G-001D | Alternator-LV Caterpillar G3306-GIDG_A044 | Replace the engine drain plugs | 1 | Y | 4 | 00 |  |  | 2232756.docx
Gidgealpa Gas Satellite - Power Generation - LV Alternator Package D Unit 663 | GIDG PWR GEN 1010-G-001D | 1010-G-001D | Alternator-LV Caterpillar G3306-GIDG_A051 | Remove and clean engine oil auto leveller | 1 | Y | 4 | 00 |  |  | 2232756.docx
Gidgealpa Gas Satellite - Power Generation - LV Alternator Package D Unit 663 | GIDG PWR GEN 1010-G-001D | 1010-G-001D | Alternator-LV Caterpillar G3306-GIDG_A01 | Check engine oil levels, check for leaks | 1 | W | 44 | 01 | 1010-G-001D 1W-44-01- | 1010-G-001D 1W-44-01- | OEC Tasks List
Gidgealpa Gas Satellite - Power Generation - LV Alternator Package D Unit 663 | GIDG PWR GEN 1010-G-001D | 1010-G-001D | Alternator-LV Caterpillar G3306-GIDG_A045 | Fill the engine with oil | 1 | Y | 4 | 00 |  |  | 2232756.docx
Gidgealpa Gas Satellite - Power Generation - LV Alternator Package D Unit 663 | GIDG PWR GEN 1010-G-001D | 1010-G-001D | Alternator-LV Caterpillar G3306-GIDG_A018 | Clean positive and negative battery terminals and cable connectors with wire brush | 2 | M | 4 | 00 |  |  | 2231773.docx
Gidgealpa Gas Satellite - Power Generation - LV Alternator Package D Unit 663 | GIDG PWR GEN 1010-G-001D | 1010-G-001D | Alternator-LV Caterpillar G3306-GIDG_A019 | Check terminal and connector for corrosion and condition | 2 | M | 4 | 00 |  |  | 2231773.docx
Gidgealpa Gas Satellite - Power Generation - LV Alternator Package E Unit 662 | GIDG PWR GEN 1010-G-001E | 1010-G-001E | Alternator-LV Caterpillar G3306-GIDG_A018 | Clean positive and negative battery terminals and cable connectors with wire brush | 2 | M | 4 | 00 |  |  | 2231773.docx
Gidgealpa Gas Satellite - Power Generation - LV Alternator Package E Unit 662 | GIDG PWR GEN 1010-GX-001E | 1010-GX-001E | Alternator-LV Package IE Caterpillar G3306-GIDG_A076 | Lubricate Alternator Bearings | 1 | Y | 01 | 00 |  |  | 2219764.docx
Gidgealpa Gas Satellite - Power Generation - LV Alternator Package E Unit 662 | GIDG PWR GEN 1010-GX-001E | 1010-GX-001E | Alternator-LV Package IE Caterpillar G3306-GIDG_A061 | Inspect exterior of alternator unit for damage, missing bolts, missing or loose covers, missing cable ties, or a build up of oil or dust | 1 | Y | 01 | 00 |  |  | 2219764.docx
Gidgealpa Gas Satellite - Power Generation - LV Alternator Package E Unit 662 | GIDG PWR GEN 1010-GX-001E | 1010-GX-001E | Alternator-LV Package IE Caterpillar G3306-GIDG_A072 | Inspect all other terminals and circuit wiring connections on the Unit Control Panel for signs of heat discolouration | 1 | Y | 01 | 00 |  |  | 2219764.docx
Gidgealpa Gas Satellite - Power Generation - LV Alternator Package E Unit 662 | GIDG PWR GEN 1010-GX-001E | 1010-GX-001E | Alternator-LV Package IE Caterpillar G3306-GIDG_A074 | Inspect the Unit Control Panel door gasket for signs of dust ingress or gaskets damage | 1 | Y | 01 | 00 |  |  | 2219764.docx
Gidgealpa Gas Satellite - Power Generation - LV Alternator Package E Unit 662 | GIDG PWR GEN 1010-GX-001E | 1010-GX-001E | Alternator-LV Package IE Caterpillar G3306-GIDG_A067 | Inspect terminals and circuit wiring connections on the AVR unit for signs of heat discolouration | 1 | Y | 01 | 00 |  |  | 2219764.docx
Gidgealpa Gas Satellite - Power Generation - LV Alternator Package E Unit 662 | GIDG PWR GEN 1010-GX-001E | 1010-GX-001E | Alternator-LV Package IE Caterpillar G3306-GIDG_A066 | Inspect the condition of all panel meters | 1 | Y | 01 | 00 |  |  | 2219764.docx
Gidgealpa Gas Satellite - Power Generation - LV Alternator Package E Unit 662 | GIDG PWR GEN 1010-GX-001E | 1010-GX-001E | Alternator-LV Package IE Caterpillar G3306-GIDG_A071 | Check the AVR heat sink cooling fins for build up of dust, clean as required | 1 | Y | 01 | 00 |  |  | 2219764.docx
Gidgealpa Gas Satellite - Power Generation - LV Alternator Package E Unit 662 | GIDG PWR GEN 1010-GX-001E | 1010-GX-001E | Alternator-LV Package IE Caterpillar G3306-GIDG_A073 | Clean and vacuum the Unit Control Panel control cabinet, ensure all heat sink cooling fins are clean | 1 | Y | 01 | 00 |  |  | 2219764.docx
Gidgealpa Gas Satellite - Power Generation - LV Alternator Package E Unit 662 | GIDG PWR GEN 1010-GX-001E | 1010-GX-001E | Alternator-LV Package IE Caterpillar G3306-GIDG_A068 | Check the security of the connections by applying force to the wires | 1 | Y | 01 | 00 |  |  | 2219764.docx
Gidgealpa Gas Satellite - Power Generation - LV Alternator Package E Unit 662 | GIDG PWR GEN 1010-GX-001E | 1010-GX-001E | Alternator-LV Package IE Caterpillar G3306-GIDG_A077 | Clean off all expelled grease | 1 | Y | 01 | 00 |  |  | 2219764.docx
Gidgealpa Gas Satellite - Power Generation - LV Alternator Package E Unit 662 | GIDG PWR GEN 1010-GX-001E | 1010-GX-001E | Alternator-LV Package IE Caterpillar G3306-GIDG_A075 | Check the circuit breaker fixing bolts for tighness | 1 | Y | 01 | 00 |  |  | 2219764.docx
Gidgealpa Gas Satellite - Power Generation - LV Alternator Package E Unit 662 | GIDG PWR GEN 1010-GX-001E | 1010-GX-001E | Alternator-LV Package IE Caterpillar G3306-GIDG_A080 | Check battery electrolyte level in each cell, top up if required with de-min water | 1 | Y | 01 | 00 |  |  | 2219764.docx
Gidgealpa Gas Satellite - Power Generation - LV Alternator Package E Unit 662 | GIDG PWR GEN 1010-GX-001E | 1010-GX-001E | Alternator-LV Package IE Caterpillar G3306-GIDG_A078 | Inspect power cabling from the Alternator to the circuit breaker | 1 | Y | 01 | 00 |  |  | 2219764.docx
Gidgealpa Gas Satellite - Power Generation - LV Alternator Package E Unit 662 | GIDG PWR GEN 1010-GX-001E | 1010-GX-001E | Alternator-LV Package IE Caterpillar G3306-GIDG_A081 | Check battery terminals for corrosion | 1 | Y | 01 | 00 |  |  | 2219764.docx
Gidgealpa Gas Satellite - Power Generation - LV Alternator Package E Unit 662 | GIDG PWR GEN 1010-GX-001E | 1010-GX-001E | Alternator-LV Package IE Caterpillar G3306-GIDG_A069 | Inspect exterior condition of AVR for damaged panels or missing screws | 1 | Y | 01 | 00 |  |  | 2219764.docx
Gidgealpa Gas Satellite - Power Generation - LV Alternator Package E Unit 662 | GIDG PWR GEN 1010-GX-001E | 1010-GX-001E | Alternator-LV Package IE Caterpillar G3306-GIDG_A060 | Check Electrical Hazard Warning signs to ensure they are securely mounted and legible | 1 | Y | 01 | 00 |  |  | 2219764.docx
Gidgealpa Gas Satellite - Power Generation - LV Alternator Package E Unit 662 | GIDG PWR GEN 1010-GX-001E | 1010-GX-001E | Alternator-LV Package IE Caterpillar G3306-GIDG_A065 | Inspect condition of all Unit Control Panel buttons for damage that prevents normal operation | 1 | Y | 01 | 00 |  |  | 2219764.docx
Gidgealpa Gas Satellite - Power Generation - LV Alternator Package E Unit 662 | GIDG PWR GEN 1010-GX-001E | 1010-GX-001E | Alternator-LV Package IE Caterpillar G3306-GIDG_A064 | Inspect all Alternator External Earth connections for signs of corrosion and check earth cable connections for tightness | 1 | Y | 01 | 00 |  |  | 2219764.docx
Gidgealpa Gas Satellite - Power Generation - LV Alternator Package E Unit 662 | GIDG PWR GEN 1010-GX-001E | 1010-GX-001E | Alternator-LV Package IE Caterpillar G3306-GIDG_A079 | Inspect power cabling for loose or missing supports, missing cable ties or contact with sharp edges / rough surfaces | 1 | Y | 01 | 00 |  |  | 2219764.docx
Gidgealpa Gas Satellite - Power Generation - LV Alternator Package E Unit 662 | GIDG PWR GEN 1010-GX-001E | 1010-GX-001E | Alternator-LV Package IE Caterpillar G3306-GIDG_A059 | Ensure all redundant items not required in the electrical panels | 1 | Y | 01 | 00 |  |  | 2219764.docx
Gidgealpa Gas Satellite - Power Generation - LV Alternator Package E Unit 662 | GIDG PWR GEN 1010-GX-001E | 1010-GX-001E | Alternator-LV Package IE Caterpillar G3306-GIDG_A070 | Inspect all electronic components and potentiometers on the AVR for signs of heat discolouration | 1 | Y | 01 | 00 |  |  | 2219764.docx
Gidgealpa Gas Satellite - Power Generation - LV Alternator Package E Unit 662 | GIDG PWR GEN 1010-GX-001E | 1010-GX-001E | Alternator-LV Package IE Caterpillar G3306-GIDG_A062 | Inspect external Earth connections at Alternator Main Terminal Box for signs of corrosion and check earth cable connections for tightness | 1 | Y | 01 | 00 |  |  | 2219764.docx
Gidgealpa Gas Satellite - Power Generation - LV Alternator Package E Unit 662 | GIDG PWR GEN 1010-GX-001E | 1010-GX-001E | Alternator-LV Package IE Caterpillar G3306-GIDG_A063 | Clean off any corrosion and repair, re-terminate or tighten connection if required | 1 | Y | 01 | 00 |  |  | 2219764.docx
Gidgealpa Gas Satellite - Power Generation - LV Alternator Package E Unit 662 | GIDG PWR GEN 1010-GX-001E | 1010-GX-001E | Alternator-LV Package IE Caterpillar G3306-GIDG_A082 | Check the battery charger amp meter, float voltage and boost voltage for expected values | 1 | Y | 01 | 00 |  |  | 2219764.docx
Gidgealpa Gas Satellite - Power Generation - LV Alternator Package E Unit 662 | GIDG PWR GEN 1010-GX-001E | 1010-GX-001E | Alternator-LV Package IE Caterpillar G3306-GIDG_A083 | Inspect the condition of all charger panel meters and ensure they operate as expected | 1 | Y | 01 | 00 |  |  | 2219764.docx
Gidgealpa Gas Satellite - Power Generation - LV Alternator Package E Unit 662 | GIDG PWR GEN 1010-GE-001E | 1010-GE-001E | Alternator-LV Caterpillar G3306-GIDG_A032 | Inspect air intake hoses for deterioration or cracks | 6 | M | 4 | 00 |  |  | 2232159.docx
Gidgealpa Gas Satellite - Power Generation - LV Alternator Package E Unit 662 | GIDG PWR GEN 1010-GE-001E | 1010-GE-001E | Alternator-LV Caterpillar G3306-GIDG_A033 | Inspect all coolant hoses and pipe joints for leaks | 6 | M | 4 | 00 |  |  | 2232159.docx
Gidgealpa Gas Satellite - Power Generation - LV Alternator Package E Unit 662 | GIDG PWR GEN 1010-GE-001E | 1010-GE-001E | Alternator-LV Caterpillar G3306-GIDG_A034 | Ensure hoses are in good condition | 6 | M | 4 | 00 |  |  | 2232159.docx
Gidgealpa Gas Satellite - Power Generation - LV Alternator Package E Unit 662 | GIDG PWR GEN 1010-GE-001E | 1010-GE-001E | Alternator-LV Caterpillar G3306-GIDG_A026 | Clean and remove any blockages | 2 | M | 4 | 00 |  |  | 2231773.docx
Gidgealpa Gas Satellite - Power Generation - LV Alternator Package E Unit 662 | GIDG PWR GEN 1010-GE-001E | 1010-GE-001E | Alternator-LV Caterpillar G3306-GIDG_A045 | Fill the engine with oil | 1 | Y | 4 | 00 |  |  | 2232756.docx
Gidgealpa Gas Satellite - Power Generation - LV Alternator Package E Unit 662 | GIDG PWR GEN 1010-GE-001E | 1010-GE-001E | Alternator-LV Caterpillar G3306-GIDG_A018 | Clean positive and negative battery terminals and cable connectors with wire brush | 2 | M | 4 | 00 |  |  | 2231773.docx
Gidgealpa Gas Satellite - Power Generation - LV Alternator Package E Unit 662 | GIDG PWR GEN 1010-GE-001E | 1010-GE-001E | Alternator-LV Caterpillar G3306-GIDG_A038 | Lubricate rear alternator bearing | 6 | M | 4 | 00 |  |  | 2232159.docx
Gidgealpa Gas Satellite - Power Generation - LV Alternator Package E Unit 662 | GIDG PWR GEN 1010-GE-001E | 1010-GE-001E | Alternator-LV Caterpillar G3306-GIDG_A025 | Check radiator cores for blockage | 2 | M | 4 | 00 |  |  | 2231773.docx
Gidgealpa Gas Satellite - Power Generation - LV Alternator Package E Unit 662 | GIDG PWR GEN 1010-GE-001E | 1010-GE-001E | Alternator-LV Caterpillar G3306-GIDG_A051 | Remove and clean engine oil auto leveller | 1 | Y | 4 | 00 |  |  | 2232756.docx
Gidgealpa Gas Satellite - Power Generation - LV Alternator Package E Unit 662 | GIDG PWR GEN 1010-GE-001E | 1010-GE-001E | Alternator-LV Caterpillar G3306-GIDG_A043 | Remove and replace the engine oil filter | 1 | Y | 4 | 00 |  |  | 2232756.docx
Gidgealpa Gas Satellite - Power Generation - LV Alternator Package E Unit 662 | GIDG PWR GEN 1010-GE-001E | 1010-GE-001E | Alternator-LV Caterpillar G3306-GIDG_A044 | Replace the engine drain plugs | 1 | Y | 4 | 00 |  |  | 2232756.docx
Gidgealpa Gas Satellite - Power Generation - LV Alternator Package E Unit 662 | GIDG PWR GEN 1010-GE-001E | 1010-GE-001E | Alternator-LV Caterpillar G3306-GIDG_A042 | Drain the oil from the engine | 1 | Y | 4 | 00 |  |  | 2232756.docx
Gidgealpa Gas Satellite - Power Generation - LV Alternator Package E Unit 662 | GIDG PWR GEN 1010-GE-001E | 1010-GE-001E | Alternator-LV Caterpillar G3306-GIDG_A02 | Check cooling system for leaks, check level and top up as required | 1 | W | 44 | 01 | 1010-GE-001E 1W-44-01- | 1010-GE-001E 1W-44-01- | OEC Tasks List
Gidgealpa Gas Satellite - Power Generation - LV Alternator Package E Unit 662 | GIDG PWR GEN 1010-GE-001E | 1010-GE-001E | Alternator-LV Caterpillar G3306-GIDG_A01 | Check engine oil levels, check for leaks | 1 | W | 44 | 01 | 1010-GE-001E 1W-44-01- | 1010-GE-001E 1W-44-01- | OEC Tasks List
Gidgealpa Gas Satellite - Power Generation - LV Alternator Package E Unit 662 | GIDG PWR GEN 1010-GE-001E | 1010-GE-001E | Alternator-LV Caterpillar G3306-GIDG_A019 | Check terminal and connector for corrosion and condition | 2 | M | 4 | 00 |  |  | 2231773.docx
Gidgealpa Gas Satellite - Power Generation - LV Alternator Package E Unit 662 | GIDG PWR GEN 1010-GE-001E | 1010-GE-001E | Alternator-LV Caterpillar G3306-GIDG_A020 | Ensure terminals are tight and apply battery protector | 2 | M | 4 | 00 |  |  | 2231773.docx
Gidgealpa Gas Satellite - Power Generation - LV Alternator Package E Unit 662 | GIDG PWR GEN 1010-GE-001E | 1010-GE-001E | Alternator-LV Caterpillar G3306-GIDG_A037 | Check wiring continuity and resistance in activated and non-activated state | 6 | M | 4 | 00 |  |  | 2232159.docx
Gidgealpa Gas Satellite - Power Generation - LV Alternator Package E Unit 662 | GIDG PWR GEN 1010-GE-001E | 1010-GE-001E | Alternator-LV Caterpillar G3306-GIDG_A035 | Check all exposed wiring for chaffing | 6 | M | 4 | 00 |  |  | 2232159.docx
Gidgealpa Gas Satellite - Power Generation - LV Alternator Package E Unit 662 | GIDG PWR GEN 1010-GE-001E | 1010-GE-001E | Alternator-LV Caterpillar G3306-GIDG_A017 | Remove battery cables at battery | 2 | M | 4 | 00 |  |  | 2231773.docx
Gidgealpa Gas Satellite - Power Generation - LV Alternator Package E Unit 662 | GIDG PWR GEN 1010-GE-001E | 1010-GE-001E | Alternator-LV Caterpillar G3306-GIDG_A041 | Inspect wiring | 6 | M | 4 | 00 |  |  | 2232574.docx
Gidgealpa Gas Satellite - Power Generation - LV Alternator Package E Unit 662 | GIDG PWR GEN 1010-GE-001E | 1010-GE-001E | Alternator-LV Caterpillar G3306-GIDG_A010 | Replace oil filter | 2 | M | 4 | 00 |  |  | 2231773.docx
Gidgealpa Gas Satellite - Power Generation - LV Alternator Package E Unit 662 | GIDG PWR GEN 1010-GE-001E | 1010-GE-001E | Alternator-LV Caterpillar G3306-GIDG_A055 | Re-dose coolant if required | 1 | Y | 4 | 00 |  |  | 2232756.docx
Gidgealpa Gas Satellite - Power Generation - LV Alternator Package E Unit 662 | GIDG PWR GEN 1010-GE-001E | 1010-GE-001E | Alternator-LV Caterpillar G3306-GIDG_A07 | Change oil using drain valves | 2 | M | 4 | 00 |  |  | 2231773.docx
Gidgealpa Gas Satellite - Power Generation - LV Alternator Package E Unit 662 | GIDG PWR GEN 1010-GE-001E | 1010-GE-001E | Alternator-LV Caterpillar G3306-GIDG_A012 | Inspect filter condition and clean or replace as required | 2 | M | 4 | 00 |  |  | 2231773.docx
Gidgealpa Gas Satellite - Power Generation - LV Alternator Package E Unit 662 | GIDG PWR GEN 1010-GE-001E | 1010-GE-001E | Alternator-LV Caterpillar G3306-GIDG_A027 | Adjust valve lash / tappets | 2 | M | 4 | 00 |  |  | 2231773.docx
Gidgealpa Gas Satellite - Power Generation - LV Alternator Package E Unit 662 | GIDG PWR GEN 1010-GE-001E | 1010-GE-001E | Alternator-LV Caterpillar G3306-GIDG_A03 | Check air filter blockage indicators, air cooling system water flow | 1 | W | 44 | 01 | 1010-GE-001E 1W-44-01- | 1010-GE-001E 1W-44-01- | OEC Tasks List
Gidgealpa Gas Satellite - Power Generation - LV Alternator Package E Unit 662 | GIDG PWR GEN 1010-GE-001E | 1010-GE-001E | Alternator-LV Caterpillar G3306-GIDG_A053 | Clean and remove any corrosion buildup | 1 | Y | 4 | 00 |  |  | 2232756.docx
Gidgealpa Gas Satellite - Power Generation - LV Alternator Package E Unit 662 | GIDG PWR GEN 1010-GE-001E | 1010-GE-001E | Alternator-LV Caterpillar G3306-GIDG_A052 | Remove leads from coils & check for corrosion | 1 | Y | 4 | 00 |  |  | 2232756.docx
Gidgealpa Gas Satellite - Power Generation - LV Alternator Package E Unit 662 | GIDG PWR GEN 1010-GE-001E | 1010-GE-001E | Alternator-LV Caterpillar G3306-GIDG_A011 | Re-fill sump with new oil to correct level | 2 | M | 4 | 00 |  |  | 2231773.docx
Gidgealpa Gas Satellite - Power Generation - LV Alternator Package E Unit 662 | GIDG PWR GEN 1010-GE-001E | 1010-GE-001E | Alternator-LV Caterpillar G3306-GIDG_A048 | Clean filter housing | 1 | Y | 4 | 00 |  |  | 2232756.docx
Gidgealpa Gas Satellite - Power Generation - LV Alternator Package E Unit 662 | GIDG PWR GEN 1010-GE-001E | 1010-GE-001E | Alternator-LV Caterpillar G3306-GIDG_A08 | Re-fit plugs and close drain line valves | 2 | M | 4 | 00 |  |  | 2231773.docx
Gidgealpa Gas Satellite - Power Generation - LV Alternator Package E Unit 662 | GIDG PWR GEN 1010-GE-001E | 1010-GE-001E | Alternator-LV Caterpillar G3306-GIDG_A049 | Replace spark plugs | 1 | Y | 4 | 00 |  |  | 2232756.docx
Gidgealpa Gas Satellite - Power Generation - LV Alternator Package E Unit 662 | GIDG PWR GEN 1010-GE-001E | 1010-GE-001E | Alternator-LV Caterpillar G3306-GIDG_A054 | Test coolant using Nalco kit | 1 | Y | 4 | 00 |  |  | 2232756.docx
Gidgealpa Gas Satellite - Power Generation - LV Alternator Package E Unit 662 | GIDG PWR GEN 1010-GE-001E | 1010-GE-001E | Alternator-LV Caterpillar G3306-GIDG_A050 | Replace radiator cap | 1 | Y | 4 | 00 |  |  | 2232756.docx
Gidgealpa Gas Satellite - Power Generation - LV Alternator Package E Unit 662 | GIDG PWR GEN 1010-GE-001E | 1010-GE-001E | Alternator-LV Caterpillar G3306-GIDG_A09 | Take oil sample | 2 | M | 4 | 00 |  |  | 2231773.docx
Gidgealpa Gas Satellite - Power Generation - LV Alternator Package E Unit 662 | GIDG PWR GEN 1010-GE-001E | 1010-GE-001E | Alternator-LV Caterpillar G3306-GIDG_A058 | Carry Out Top End Overhaul | 3 | Y | 4 | 00 |  |  | 2256646.docx
Gidgealpa Gas Satellite - Power Generation - LV Alternator Package E Unit 662 | GIDG PWR GEN 1010-GE-001E | 1010-GE-001E | Alternator-LV Caterpillar G3306-GIDG_A013 | Clean filter and housing | 2 | M | 4 | 00 |  |  | 2231773.docx
Gidgealpa Gas Satellite - Power Generation - LV Alternator Package E Unit 662 | GIDG PWR GEN 1010-GE-001E | 1010-GE-001E | Alternator-LV Caterpillar G3306-GIDG_A057 | Carry out Unit Overhaul | 3 | Y | 4 | 00 |  |  | 2222484.docx
Gidgealpa Gas Satellite - Power Generation - LV Alternator Package E Unit 662 | GIDG PWR GEN 1010-GE-001E | 1010-GE-001E | Alternator-LV Caterpillar G3306-GIDG_A024 | Check coolant level | 2 | M | 4 | 00 |  |  | 2231773.docx
Gidgealpa Gas Satellite - Power Generation - LV Alternator Package E Unit 662 | GIDG PWR GEN 1010-GE-001E | 1010-GE-001E | Alternator-LV Caterpillar G3306-GIDG_A016 | Check the electrolyte level in the batteries and top up as required | 2 | M | 4 | 00 |  |  | 2231773.docx
Gidgealpa Gas Satellite - Power Generation - LV Alternator Package E Unit 662 | GIDG PWR GEN 1010-GE-001E | 1010-GE-001E | Alternator-LV Caterpillar G3306-GIDG_A023 | Replace fan belt or alternator belt | 2 | M | 4 | 00 |  |  | 2231773.docx
Gidgealpa Gas Satellite - Power Generation - LV Alternator Package E Unit 662 | GIDG PWR GEN 1010-GE-001E | 1010-GE-001E | Alternator-LV Caterpillar G3306-GIDG_A022 | Check fan belt condition | 2 | M | 4 | 00 |  |  | 2231773.docx
Gidgealpa Gas Satellite - Power Generation - LV Alternator Package E Unit 662 | GIDG PWR GEN 1010-GE-001E | 1010-GE-001E | Alternator-LV Caterpillar G3306-GIDG_A030 | Clean crankcase breather | 2 | M | 4 | 00 |  |  | 2231773.docx
Gidgealpa Gas Satellite - Power Generation - LV Alternator Package E Unit 662 | GIDG PWR GEN 1010-GE-001E | 1010-GE-001E | Alternator-LV Caterpillar G3306-GIDG_A014 | Replace air filter element and clean housing | 2 | M | 4 | 00 |  |  | 2231773.docx
Gidgealpa Gas Satellite - Power Generation - LV Alternator Package E Unit 662 | GIDG PWR GEN 1010-GE-001E | 1010-GE-001E | Alternator-LV Caterpillar G3306-GIDG_A028 | Check and adjust intake and exhaust valve lash | 2 | M | 4 | 00 |  |  | 2231773.docx
Gidgealpa Gas Satellite - Power Generation - LV Alternator Package E Unit 662 | GIDG PWR GEN 1010-GE-001E | 1010-GE-001E | Alternator-LV Caterpillar G3306-GIDG_A040 | Ensure alignment of drive has not altered If replacements or re-tensioning | 6 | M | 4 | 00 |  |  | 2232574.docx
Gidgealpa Gas Satellite - Power Generation - LV Alternator Package E Unit 662 | GIDG PWR GEN 1010-GE-001E | 1010-GE-001E | Alternator-LV Caterpillar G3306-GIDG_A031 | Lubricate carburettor linkage | 2 | M | 4 | 00 |  |  | 2231773.docx
Gidgealpa Gas Satellite - Power Generation - LV Alternator Package E Unit 662 | GIDG PWR GEN 1010-GE-001E | 1010-GE-001E | Alternator-LV Caterpillar G3306-GIDG_A015 | Clean oil header tank sight glasses & breather | 2 | M | 4 | 00 |  |  | 2231773.docx
Gidgealpa Gas Satellite - Power Generation - LV Alternator Package E Unit 662 | GIDG PWR GEN 1010-GE-001E | 1010-GE-001E | Alternator-LV Caterpillar G3306-GIDG_A029 | Re-fit existing rocker cover gasket and tension rocker cover | 2 | M | 4 | 00 |  |  | 2231773.docx
Gidgealpa Gas Satellite - Power Generation - LV Alternator Package E Unit 662 | GIDG PWR GEN 1010-GE-001E | 1010-GE-001E | Alternator-LV Caterpillar G3306-GIDG_A047 | Replace air filter element | 1 | Y | 4 | 00 |  |  | 2232756.docx
Gidgealpa Gas Satellite - Power Generation - LV Alternator Package E Unit 662 | GIDG PWR GEN 1010-GE-001E | 1010-GE-001E | Alternator-LV Caterpillar G3306-GIDG_A021 | Lubricate fan drive & Idler pulley | 2 | M | 4 | 00 |  |  | 2231773.docx
Gidgealpa Gas Satellite - Power Generation - LV Alternator Package E Unit 662 | GIDG PWR GEN 1010-GE-001E | 1010-GE-001E | Alternator-LV Caterpillar G3306-GIDG_A06 | For Emergency Diesel Generator, Check diesel Fuel level | 1 | W | 44 | 01 | 1010-GE-001E 1W-44-01- | 1010-GE-001E 1W-44-01- | OEC Tasks List
Gidgealpa Gas Satellite - Power Generation - LV Alternator Package E Unit 662 | GIDG PWR GEN 1010-GE-001E | 1010-GE-001E | Alternator-LV Caterpillar G3306-GIDG_A046 | Inspect the engine fill and drain points for visible oil leaks, clean and repair as required | 1 | Y | 4 | 00 |  |  | 2232756.docx
Gidgealpa Gas Satellite - Power Generation - LV Alternator Package E Unit 662 | GIDG PWR GEN 1010-GE-001E | 1010-GE-001E | Alternator-LV Caterpillar G3306-GIDG_A05 | For Emergency Diesel Generator, Start the set and run to check running condition | 1 | W | 44 | 01 | 1010-GE-001E 1W-44-01- | 1010-GE-001E 1W-44-01- | OEC Tasks List
Gidgealpa Gas Satellite - Power Generation - LV Alternator Package E Unit 662 | GIDG PWR GEN 1010-GE-001E | 1010-GE-001E | Alternator-LV Caterpillar G3306-GIDG_A04 | Check for abnormal noise from engine | 1 | W | 44 | 01 | 1010-GE-001E 1W-44-01- | 1010-GE-001E 1W-44-01- | OEC Tasks List
Gidgealpa Gas Satellite - Power Generation - LV Alternator Package E Unit 662 | GIDG PWR GEN 1010-GE-001E | 1010-GE-001E | Alternator-LV Caterpillar G3306-GIDG_A039 | Inspect engine mounts for cracks or looseness | 6 | M | 4 | 00 |  |  | 2232574.docx
Gidgealpa Gas Satellite - Power Generation - LV Alternator Package E Unit 662 | GIDG PWR GEN 1010-GE-001E | 1010-GE-001E | Alternator-LV Caterpillar G3306-GIDG_A036 | Function test oil press low shutdown switch | 6 | M | 4 | 00 |  |  | 2232159.docx
Gidgealpa Gas Satellite - Power Generation - LV Alternator Package E Unit 662 | GIDG PWR GEN 1010-GE-001E | 1010-GE-001E | Alternator-LV Caterpillar G3306-GIDG_A056 | Replace cylinder head temp shutdown switch | 1 | Y | 01 | 00 |  |  | 2232756.docx
Gidgealpa Gas Satellite - Power Generation - LV Alternator Package E Unit 662 | GIDG PWR GEN 1010-G-001E | 1010-G-001E | Alternator-LV Caterpillar G3306-GIDG_A025 | Check radiator cores for blockage | 2 | M | 4 | 00 |  |  | 2231773.docx
Gidgealpa Gas Satellite - Power Generation - LV Alternator Package E Unit 662 | GIDG PWR GEN 1010-G-001E | 1010-G-001E | Alternator-LV Caterpillar G3306-GIDG_A033 | Inspect all coolant hoses and pipe joints for leaks | 6 | M | 4 | 00 |  |  | 2232159.docx
Gidgealpa Gas Satellite - Power Generation - LV Alternator Package E Unit 662 | GIDG PWR GEN 1010-G-001E | 1010-G-001E | Alternator-LV Caterpillar G3306-GIDG_A026 | Clean and remove any blockages | 2 | M | 4 | 00 |  |  | 2231773.docx
Gidgealpa Gas Satellite - Power Generation - LV Alternator Package E Unit 662 | GIDG PWR GEN 1010-G-001E | 1010-G-001E | Alternator-LV Caterpillar G3306-GIDG_A034 | Ensure hoses are in good condition | 6 | M | 4 | 00 |  |  | 2232159.docx
Gidgealpa Gas Satellite - Power Generation - LV Alternator Package E Unit 662 | GIDG PWR GEN 1010-G-001E | 1010-G-001E | Alternator-LV Caterpillar G3306-GIDG_A032 | Inspect air intake hoses for deterioration or cracks | 6 | M | 4 | 00 |  |  | 2232159.docx
Gidgealpa Gas Satellite - Power Generation - LV Alternator Package E Unit 662 | GIDG PWR GEN 1010-G-001E | 1010-G-001E | Alternator-LV Caterpillar G3306-GIDG_A038 | Lubricate rear alternator bearing | 6 | M | 4 | 00 |  |  | 2232159.docx
Gidgealpa Gas Satellite - Power Generation - LV Alternator Package E Unit 662 | GIDG PWR GEN 1010-G-001E | 1010-G-001E | Alternator-LV Caterpillar G3306-GIDG_A036 | Function test oil press low shutdown switch | 6 | M | 4 | 00 |  |  | 2232159.docx
Gidgealpa Gas Satellite - Power Generation - LV Alternator Package E Unit 662 | GIDG PWR GEN 1010-G-001E | 1010-G-001E | Alternator-LV Caterpillar G3306-GIDG_A056 | Replace cylinder head temp shutdown switch | 1 | Y | 01 | 00 |  |  | 2232756.docx
Gidgealpa Gas Satellite - Power Generation - LV Alternator Package E Unit 662 | GIDG PWR GEN 1010-G-001E | 1010-G-001E | Alternator-LV Caterpillar G3306-GIDG_A04 | Check for abnormal noise from engine | 1 | W | 44 | 01 | 1010-G-001E 1W-44-01- | 1010-G-001E 1W-44-01- | OEC Tasks List
Gidgealpa Gas Satellite - Power Generation - LV Alternator Package E Unit 662 | GIDG PWR GEN 1010-G-001E | 1010-G-001E | Alternator-LV Caterpillar G3306-GIDG_A046 | Inspect the engine fill and drain points for visible oil leaks, clean and repair as required | 1 | Y | 4 | 00 |  |  | 2232756.docx
Gidgealpa Gas Satellite - Power Generation - LV Alternator Package E Unit 662 | GIDG PWR GEN 1010-G-001E | 1010-G-001E | Alternator-LV Caterpillar G3306-GIDG_A06 | For Emergency Diesel Generator, Check diesel Fuel level | 1 | W | 44 | 01 | 1010-G-001E 1W-44-01- | 1010-G-001E 1W-44-01- | OEC Tasks List
Gidgealpa Gas Satellite - Power Generation - LV Alternator Package E Unit 662 | GIDG PWR GEN 1010-G-001E | 1010-G-001E | Alternator-LV Caterpillar G3306-GIDG_A039 | Inspect engine mounts for cracks or looseness | 6 | M | 4 | 00 |  |  | 2232574.docx
Gidgealpa Gas Satellite - Power Generation - LV Alternator Package E Unit 662 | GIDG PWR GEN 1010-G-001E | 1010-G-001E | Alternator-LV Caterpillar G3306-GIDG_A05 | For Emergency Diesel Generator, Start the set and run to check running condition | 1 | W | 44 | 01 | 1010-G-001E 1W-44-01- | 1010-G-001E 1W-44-01- | OEC Tasks List
Gidgealpa Gas Satellite - Power Generation - LV Alternator Package E Unit 662 | GIDG PWR GEN 1010-G-001E | 1010-G-001E | Alternator-LV Caterpillar G3306-GIDG_A02 | Check cooling system for leaks, check level and top up as required | 1 | W | 44 | 01 | 1010-G-001E 1W-44-01- | 1010-G-001E 1W-44-01- | OEC Tasks List
Gidgealpa Gas Satellite - Power Generation - LV Alternator Package E Unit 662 | GIDG PWR GEN 1010-G-001E | 1010-G-001E | Alternator-LV Caterpillar G3306-GIDG_A042 | Drain the oil from the engine | 1 | Y | 4 | 00 |  |  | 2232756.docx
Gidgealpa Gas Satellite - Power Generation - LV Alternator Package E Unit 662 | GIDG PWR GEN 1010-G-001E | 1010-G-001E | Alternator-LV Caterpillar G3306-GIDG_A047 | Replace air filter element | 1 | Y | 4 | 00 |  |  | 2232756.docx
Gidgealpa Gas Satellite - Power Generation - LV Alternator Package E Unit 662 | GIDG PWR GEN 1010-G-001E | 1010-G-001E | Alternator-LV Caterpillar G3306-GIDG_A029 | Re-fit existing rocker cover gasket and tension rocker cover | 2 | M | 4 | 00 |  |  | 2231773.docx
Gidgealpa Gas Satellite - Power Generation - LV Alternator Package E Unit 662 | GIDG PWR GEN 1010-G-001E | 1010-G-001E | Alternator-LV Caterpillar G3306-GIDG_A021 | Lubricate fan drive & Idler pulley | 2 | M | 4 | 00 |  |  | 2231773.docx
Gidgealpa Gas Satellite - Power Generation - LV Alternator Package E Unit 662 | GIDG PWR GEN 1010-G-001E | 1010-G-001E | Alternator-LV Caterpillar G3306-GIDG_A043 | Remove and replace the engine oil filter | 1 | Y | 4 | 00 |  |  | 2232756.docx
Gidgealpa Gas Satellite - Power Generation - LV Alternator Package E Unit 662 | GIDG PWR GEN 1010-G-001E | 1010-G-001E | Alternator-LV Caterpillar G3306-GIDG_A045 | Fill the engine with oil | 1 | Y | 4 | 00 |  |  | 2232756.docx
Gidgealpa Gas Satellite - Power Generation - LV Alternator Package E Unit 662 | GIDG PWR GEN 1010-G-001E | 1010-G-001E | Alternator-LV Caterpillar G3306-GIDG_A044 | Replace the engine drain plugs | 1 | Y | 4 | 00 |  |  | 2232756.docx
Gidgealpa Gas Satellite - Power Generation - LV Alternator Package E Unit 662 | GIDG PWR GEN 1010-G-001E | 1010-G-001E | Alternator-LV Caterpillar G3306-GIDG_A051 | Remove and clean engine oil auto leveller | 1 | Y | 4 | 00 |  |  | 2232756.docx
Gidgealpa Gas Satellite - Power Generation - LV Alternator Package E Unit 662 | GIDG PWR GEN 1010-G-001E | 1010-G-001E | Alternator-LV Caterpillar G3306-GIDG_A01 | Check engine oil levels, check for leaks | 1 | W | 44 | 01 | 1010-G-001E 1W-44-01- | 1010-G-001E 1W-44-01- | OEC Tasks List
Gidgealpa Gas Satellite - Power Generation - LV Alternator Package E Unit 662 | GIDG PWR GEN 1010-G-001E | 1010-G-001E | Alternator-LV Caterpillar G3306-GIDG_A03 | Check air filter blockage indicators, air cooling system water flow | 1 | W | 44 | 01 | 1010-G-001E 1W-44-01- | 1010-G-001E 1W-44-01- | OEC Tasks List
Gidgealpa Gas Satellite - Power Generation - LV Alternator Package E Unit 662 | GIDG PWR GEN 1010-G-001E | 1010-G-001E | Alternator-LV Caterpillar G3306-GIDG_A024 | Check coolant level | 2 | M | 4 | 00 |  |  | 2231773.docx
Gidgealpa Gas Satellite - Power Generation - LV Alternator Package E Unit 662 | GIDG PWR GEN 1010-G-001E | 1010-G-001E | Alternator-LV Caterpillar G3306-GIDG_A027 | Adjust valve lash / tappets | 2 | M | 4 | 00 |  |  | 2231773.docx
Gidgealpa Gas Satellite - Power Generation - LV Alternator Package E Unit 662 | GIDG PWR GEN 1010-G-001E | 1010-G-001E | Alternator-LV Caterpillar G3306-GIDG_A053 | Clean and remove any corrosion buildup | 1 | Y | 4 | 00 |  |  | 2232756.docx
Gidgealpa Gas Satellite - Power Generation - LV Alternator Package E Unit 662 | GIDG PWR GEN 1010-G-001E | 1010-G-001E | Alternator-LV Caterpillar G3306-GIDG_A023 | Replace fan belt or alternator belt | 2 | M | 4 | 00 |  |  | 2231773.docx
Gidgealpa Gas Satellite - Power Generation - LV Alternator Package E Unit 662 | GIDG PWR GEN 1010-G-001E | 1010-G-001E | Alternator-LV Caterpillar G3306-GIDG_A014 | Replace air filter element and clean housing | 2 | M | 4 | 00 |  |  | 2231773.docx
Gidgealpa Gas Satellite - Power Generation - LV Alternator Package E Unit 662 | GIDG PWR GEN 1010-G-001E | 1010-G-001E | Alternator-LV Caterpillar G3306-GIDG_A030 | Clean crankcase breather | 2 | M | 4 | 00 |  |  | 2231773.docx
Gidgealpa Gas Satellite - Power Generation - LV Alternator Package E Unit 662 | GIDG PWR GEN 1010-G-001E | 1010-G-001E | Alternator-LV Caterpillar G3306-GIDG_A016 | Check the electrolyte level in the batteries and top up as required | 2 | M | 4 | 00 |  |  | 2231773.docx
Gidgealpa Gas Satellite - Power Generation - LV Alternator Package E Unit 662 | GIDG PWR GEN 1010-G-001E | 1010-G-001E | Alternator-LV Caterpillar G3306-GIDG_A040 | Ensure alignment of drive has not altered If replacements or re-tensioning | 6 | M | 4 | 00 |  |  | 2232574.docx
Gidgealpa Gas Satellite - Power Generation - LV Alternator Package E Unit 662 | GIDG PWR GEN 1010-G-001E | 1010-G-001E | Alternator-LV Caterpillar G3306-GIDG_A031 | Lubricate carburettor linkage | 2 | M | 4 | 00 |  |  | 2231773.docx
Gidgealpa Gas Satellite - Power Generation - LV Alternator Package E Unit 662 | GIDG PWR GEN 1010-G-001E | 1010-G-001E | Alternator-LV Caterpillar G3306-GIDG_A028 | Check and adjust intake and exhaust valve lash | 2 | M | 4 | 00 |  |  | 2231773.docx
Gidgealpa Gas Satellite - Power Generation - LV Alternator Package E Unit 662 | GIDG PWR GEN 1010-G-001E | 1010-G-001E | Alternator-LV Caterpillar G3306-GIDG_A022 | Check fan belt condition | 2 | M | 4 | 00 |  |  | 2231773.docx
Gidgealpa Gas Satellite - Power Generation - LV Alternator Package E Unit 662 | GIDG PWR GEN 1010-G-001E | 1010-G-001E | Alternator-LV Caterpillar G3306-GIDG_A015 | Clean oil header tank sight glasses & breather | 2 | M | 4 | 00 |  |  | 2231773.docx
Gidgealpa Gas Satellite - Power Generation - LV Alternator Package E Unit 662 | GIDG PWR GEN 1010-G-001E | 1010-G-001E | Alternator-LV Caterpillar G3306-GIDG_A055 | Re-dose coolant if required | 1 | Y | 4 | 00 |  |  | 2232756.docx
Gidgealpa Gas Satellite - Power Generation - LV Alternator Package E Unit 662 | GIDG PWR GEN 1010-G-001E | 1010-G-001E | Alternator-LV Caterpillar G3306-GIDG_A058 | Carry Out Top End Overhaul | 3 | Y | 4 | 00 |  |  | 2256646.docx
Gidgealpa Gas Satellite - Power Generation - LV Alternator Package E Unit 662 | GIDG PWR GEN 1010-G-001E | 1010-G-001E | Alternator-LV Caterpillar G3306-GIDG_A057 | Carry out Unit Overhaul | 3 | Y | 4 | 00 |  |  | 2222484.docx
Gidgealpa Gas Satellite - Power Generation - LV Alternator Package E Unit 662 | GIDG PWR GEN 1010-G-001E | 1010-G-001E | Alternator-LV Caterpillar G3306-GIDG_A054 | Test coolant using Nalco kit | 1 | Y | 4 | 00 |  |  | 2232756.docx
Gidgealpa Gas Satellite - Power Generation - LV Alternator Package E Unit 662 | GIDG PWR GEN 1010-G-001E | 1010-G-001E | Alternator-LV Caterpillar G3306-GIDG_A048 | Clean filter housing | 1 | Y | 4 | 00 |  |  | 2232756.docx
Gidgealpa Gas Satellite - Power Generation - LV Alternator Package E Unit 662 | GIDG PWR GEN 1010-G-001E | 1010-G-001E | Alternator-LV Caterpillar G3306-GIDG_A052 | Remove leads from coils & check for corrosion | 1 | Y | 4 | 00 |  |  | 2232756.docx
Gidgealpa Gas Satellite - Power Generation - LV Alternator Package E Unit 662 | GIDG PWR GEN 1010-G-001E | 1010-G-001E | Alternator-LV Caterpillar G3306-GIDG_A050 | Replace radiator cap | 1 | Y | 4 | 00 |  |  | 2232756.docx
Gidgealpa Gas Satellite - Power Generation - LV Alternator Package E Unit 662 | GIDG PWR GEN 1010-G-001E | 1010-G-001E | Alternator-LV Caterpillar G3306-GIDG_A012 | Inspect filter condition and clean or replace as required | 2 | M | 4 | 00 |  |  | 2231773.docx
Gidgealpa Gas Satellite - Power Generation - LV Alternator Package E Unit 662 | GIDG PWR GEN 1010-G-001E | 1010-G-001E | Alternator-LV Caterpillar G3306-GIDG_A010 | Replace oil filter | 2 | M | 4 | 00 |  |  | 2231773.docx
Gidgealpa Gas Satellite - Power Generation - LV Alternator Package E Unit 662 | GIDG PWR GEN 1010-G-001E | 1010-G-001E | Alternator-LV Caterpillar G3306-GIDG_A09 | Take oil sample | 2 | M | 4 | 00 |  |  | 2231773.docx
Gidgealpa Gas Satellite - Power Generation - LV Alternator Package E Unit 662 | GIDG PWR GEN 1010-G-001E | 1010-G-001E | Alternator-LV Caterpillar G3306-GIDG_A07 | Change oil using drain valves | 2 | M | 4 | 00 |  |  | 2231773.docx
Gidgealpa Gas Satellite - Power Generation - LV Alternator Package E Unit 662 | GIDG PWR GEN 1010-G-001E | 1010-G-001E | Alternator-LV Caterpillar G3306-GIDG_A08 | Re-fit plugs and close drain line valves | 2 | M | 4 | 00 |  |  | 2231773.docx
Gidgealpa Gas Satellite - Power Generation - LV Alternator Package E Unit 662 | GIDG PWR GEN 1010-G-001E | 1010-G-001E | Alternator-LV Caterpillar G3306-GIDG_A049 | Replace spark plugs | 1 | Y | 4 | 00 |  |  | 2232756.docx
Gidgealpa Gas Satellite - Power Generation - LV Alternator Package E Unit 662 | GIDG PWR GEN 1010-G-001E | 1010-G-001E | Alternator-LV Caterpillar G3306-GIDG_A013 | Clean filter and housing | 2 | M | 4 | 00 |  |  | 2231773.docx
Gidgealpa Gas Satellite - Power Generation - LV Alternator Package E Unit 662 | GIDG PWR GEN 1010-G-001E | 1010-G-001E | Alternator-LV Caterpillar G3306-GIDG_A011 | Re-fill sump with new oil to correct level | 2 | M | 4 | 00 |  |  | 2231773.docx
Gidgealpa Gas Satellite - Power Generation - LV Alternator Package E Unit 662 | GIDG PWR GEN 1010-G-001E | 1010-G-001E | Alternator-LV Caterpillar G3306-GIDG_A041 | Inspect wiring | 6 | M | 4 | 00 |  |  | 2232574.docx
Gidgealpa Gas Satellite - Power Generation - LV Alternator Package E Unit 662 | GIDG PWR GEN 1010-G-001E | 1010-G-001E | Alternator-LV Caterpillar G3306-GIDG_A037 | Check wiring continuity and resistance in activated and non-activated state | 6 | M | 4 | 00 |  |  | 2232159.docx
Gidgealpa Gas Satellite - Power Generation - LV Alternator Package E Unit 662 | GIDG PWR GEN 1010-G-001E | 1010-G-001E | Alternator-LV Caterpillar G3306-GIDG_A017 | Remove battery cables at battery | 2 | M | 4 | 00 |  |  | 2231773.docx
Gidgealpa Gas Satellite - Power Generation - LV Alternator Package E Unit 662 | GIDG PWR GEN 1010-G-001E | 1010-G-001E | Alternator-LV Caterpillar G3306-GIDG_A035 | Check all exposed wiring for chaffing | 6 | M | 4 | 00 |  |  | 2232159.docx
Gidgealpa Gas Satellite - Power Generation - LV Alternator Package E Unit 662 | GIDG PWR GEN 1010-G-001E | 1010-G-001E | Alternator-LV Caterpillar G3306-GIDG_A019 | Check terminal and connector for corrosion and condition | 2 | M | 4 | 00 |  |  | 2231773.docx
Gidgealpa Gas Satellite - Power Generation - LV Alternator Package E Unit 662 | GIDG PWR GEN 1010-G-001E | 1010-G-001E | Alternator-LV Caterpillar G3306-GIDG_A020 | Ensure terminals are tight and apply battery protector | 2 | M | 4 | 00 |  |  | 2231773.docx
Gidgealpa Gas Satellite - Shutdown - Emergency Shutdown | GIDG SHUT 1010-PT-00469 | 1010-PT-00469 | Transmitter-Pressure Rosemount 3051S-GIDG_A01 | Change Rosemount 3051S Wireless Level Transmitter Battery Pack | 2 | Y | 01 | 00 |  |  | SERVICE-PM-IP.PS-003628-C-0001.docx
Gidgealpa Gas Satellite - Shutdown - Mawson Kurunda Separator | GIDG SHUT 1010-LY-01080A | 1010-LY-01080A | Transmitter-Level Rosemount 3051S-GIDG_A01 | Change Rosemount 3051S Wireless Level Transmitter Battery Pack | 2 | Y | 01 | 00 |  |  | SERVICE-PM-IP.LS-003628-C-0001.docx
Gidgealpa Gas Satellite - Shutdown - Mawson Kurunda Separator | GIDG SHUT 1010-PT-01095A | 1010-PT-01095A | Transmitter-Pressure Rosemount 3051S-GIDG_A01 | Change Rosemount 3051S Wireless Level Transmitter Battery Pack | 2 | Y | 01 | 00 |  |  | SERVICE-PM-IP.PS-003628-C-0001.docx
Gidgealpa Gas Satellite - Shutdown - Mawson Kurunda Separator | GIDG SHUT 1010-PT-01094 | 1010-PT-01094 | Transmitter-Pressure Rosemount 3051S-GIDG_A01 | Change Rosemount 3051S Wireless Level Transmitter Battery Pack | 2 | Y | 01 | 00 |  |  | SERVICE-PM-IP.PS-003628-C-0001.docx
Gidgealpa Gas Satellite - Shutdown - Mawson Kurunda Separator | GIDG SHUT 1010-PT-00125 | 1010-PT-00125 | Transmitter-Pressure Rosemount 3051S-GIDG_A01 | Change Rosemount 3051S Wireless Level Transmitter Battery Pack | 2 | Y | 01 | 00 |  |  | SERVICE-PM-IP.PS-003628-C-0001.docx
Gidgealpa Gas Satellite - Shutdown - Mawson Kurunda Separator | GIDG SHUT 1010-LY-01090B | 1010-LY-01090B | Transmitter-Level Rosemount 3051S-GIDG_A01 | Change Rosemount 3051S Wireless Level Transmitter Battery Pack | 2 | Y | 01 | 00 |  |  | SERVICE-PM-IP.LS-003628-C-0001.docx
Gidgealpa Gas Satellite - Shutdown - Mawson Kurunda Separator | GIDG SHUT 1010-LY-01090A | 1010-LY-01090A | Transmitter-Level Rosemount 3051S-GIDG_A01 | Change Rosemount 3051S Wireless Level Transmitter Battery Pack | 2 | Y | 01 | 00 |  |  | SERVICE-PM-IP.LS-003628-C-0001.docx
Gidgealpa Gas Satellite - Shutdown - Mawson Kurunda Separator | GIDG SHUT 1010-LY-01080B | 1010-LY-01080B | Transmitter-Level Rosemount 3051S-GIDG_A01 | Change Rosemount 3051S Wireless Level Transmitter Battery Pack | 2 | Y | 01 | 00 |  |  | SERVICE-PM-IP.LS-003628-C-0001.docx