## Sheet1
Action ID | Package ID | Package Decription | Package Groups | Strategy ID | Strategy | ID | Asset Name | Interval | Interval Units | Recommended Resource | Shutdown Required | Reference Column | Job Plan ID | Action Name | Plan Description | MyPlant Document Number | Oracle Activity
HVAC-TICK_A02 | Tickalara Satellite - Buildings - Office | Tickalara Satellite - Buildings - Office | 3800 - Tickalara Satellite | KICK BLD 3800-SAT-BLD | KICK | BLD | 3800-SAT-BLD | 6 | M | 11 | 00 | KICK BLD 6M-11-00 | KICK BLD 6M-11-00-001 | Carry out service on split system (Indoor unit) | South West Queensland Air Conditioning 6 Month Service - Route E | SERVICE-PM-SR.BU-900168-J-2001.docx | 2216177 | 001
HVAC-TICK_A02 | Tickalara Satellite - Buildings - Office | Tickalara Satellite - Buildings - Office | 3800 - Tickalara Satellite | KICK BLD 3800-SAT-BLD | KICK | BLD | 3800-SAT-BLD | 6 | M | 11 | 00 | KICK BLD 6M-11-00 | KICK BLD 6M-11-00-001 | Carry out service on split system (Outdoor unit) | South West Queensland Air Conditioning 6 Month Service - Route E | SERVICE-PM-SR.BU-900168-J-2001.docx | 2216177 | 001
HVAC-TICK_A02 | Tickalara Satellite - Buildings - Office | Tickalara Satellite - Buildings - Office | 3800 - Tickalara Satellite | KICK BLD 3800-SAT-BLD | KICK | BLD | 3800-SAT-BLD | 12 | M | 11 | 00 | KICK BLD 12M-11-00 | KICK BLD 12M-11-00-001 | Carry out service on RAC | South West Queensland Air Conditioning Annual Service - Route E | SERVICE-PM-SR.BU-900168-J-2004.docx | 2702381 | 001
Hatch-Tank-TICK_A01 | Tickalara Satellite - Crude Oil Storage - Dewatering / Test Tanks | Tickalara Satellite - Crude Oil Storage - Dewatering / Test Tanks | 3800 - Tickalara Satellite | KICK CRUDE OIL STRG 3800-TK-001B | KICK | CRUDE OIL STRG | 3800-TK-001B | 12 | M | 04 | 00 | KICK CRUDE OIL STRG 12M-04-00 | KICK CRUDE OIL STRG 12M-04-00-001 | Visually inspect pins for wear and replace as required | Dewatering Tank 1B - 1C Annual Explosive Hatch Mechanical Service | 2239059.docx | 2239059 | 001
Hatch-Tank-TICK_A01 | Tickalara Satellite - Crude Oil Storage - Dewatering / Test Tanks | Tickalara Satellite - Crude Oil Storage - Dewatering / Test Tanks | 3800 - Tickalara Satellite | KICK CRUDE OIL STRG 3800-TK-001C | KICK | CRUDE OIL STRG | 3800-TK-001C | 12 | M | 04 | 00 | KICK CRUDE OIL STRG 12M-04-00 | KICK CRUDE OIL STRG 12M-04-00-001 | Visually inspect pins for wear and replace as required | Dewatering Tank 1B - 1C Annual Explosive Hatch Mechanical Service | 2239059.docx | 2239059 | 001
Hatch-Tank-TICK_A01 | Tickalara Satellite - Crude Oil Storage - Dewatering / Test Tanks | Tickalara Satellite - Crude Oil Storage - Dewatering / Test Tanks | 3800 - Tickalara Satellite | KICK CRUDE OIL STRG 3800-TK-001C | KICK | CRUDE OIL STRG | 3800-TK-001C | 12 | M | 04 | 00 | KICK CRUDE OIL STRG 12M-04-00 | KICK CRUDE OIL STRG 12M-04-00-001 | Visually inspect explosive hatch for holes and cracks | Dewatering Tank 1B - 1C Annual Explosive Hatch Mechanical Service | 2239059.docx | 2239059 | 001
Hatch-Tank-TICK_A01 | Tickalara Satellite - Crude Oil Storage - Dewatering / Test Tanks | Tickalara Satellite - Crude Oil Storage - Dewatering / Test Tanks | 3800 - Tickalara Satellite | KICK CRUDE OIL STRG 3800-TK-001B | KICK | CRUDE OIL STRG | 3800-TK-001B | 12 | M | 04 | 00 | KICK CRUDE OIL STRG 12M-04-00 | KICK CRUDE OIL STRG 12M-04-00-001 | Visually inspect explosive hatch for holes and cracks | Dewatering Tank 1B - 1C Annual Explosive Hatch Mechanical Service | 2239059.docx | 2239059 | 001
Meter-Flow-TICK_A01 | Tickalara Satellite - Export - Control and Monitor | Tickalara Satellite - Export - Control and Monitor | 3800 - Tickalara Satellite | KICK EXP 3800-FE-0129 | KICK | EXP | 3800-FE-0129 | 5 | Y | 01 | 00 | KICK EXP 5Y-01-00 | KICK EXP 5Y-01-00-001 | Re-certification export metering master flow meter | Tickalara Export Metering Master Flow Meter for Five Yearly Re-Certification | 2241340.docx | 2241340 | 001
Pump-Plunger Duraqual PF753-135L65-TICK_A012 | Tickalara Satellite - Export - Shipping Pumps | Tickalara Satellite - Export - Shipping Pumps | 3800 - Tickalara Satellite | KICK EXP 3800-P-001A | KICK | EXP | 3800-P-001A | 12 | M | 01 | 00 | KICK EXP 12M-01-00 | KICK EXP 12M-01-00-001 | Overhaul High Engine Water Temperature Shutdown Switch | Tickalara Duraqual Shipping Pump PF753 Panel Inst/Elec Service | 2644909.docx | 2644909 | 001
Pump-Plunger Duraqual PF753-135L65-TICK_A012 | Tickalara Satellite - Export - Shipping Pumps | Tickalara Satellite - Export - Shipping Pumps | 3800 - Tickalara Satellite | KICK EXP 3800-P-001B | KICK | EXP | 3800-P-001B | 12 | M | 01 | 00 | KICK EXP 12M-01-00 | KICK EXP 12M-01-00-001 | Overhaul High Engine Water Temperature Shutdown Switch | Tickalara Duraqual Shipping Pump PF753 Panel Inst/Elec Service | 2644909.docx | 2644909 | 001
Pump-Plunger Duraqual PF753-135L65-TICK_A012 | Tickalara Satellite - Export - Shipping Pumps | Tickalara Satellite - Export - Shipping Pumps | 3800 - Tickalara Satellite | KICK EXP 3800-P-001B | KICK | EXP | 3800-P-001B | 12 | M | 01 | 00 | KICK EXP 12M-01-00 | KICK EXP 12M-01-00-001 | Overhaul High Engine Oil Temperature Shutdown Switch | Tickalara Duraqual Shipping Pump PF753 Panel Inst/Elec Service | 2644909.docx | 2644909 | 001
Pump-Plunger Duraqual PF753-135L65-TICK_A012 | Tickalara Satellite - Export - Shipping Pumps | Tickalara Satellite - Export - Shipping Pumps | 3800 - Tickalara Satellite | KICK EXP 3800-P-001B | KICK | EXP | 3800-P-001B | 12 | M | 01 | 00 | KICK EXP 12M-01-00 | KICK EXP 12M-01-00-001 | Overhaul Low Engine Water Flow Shutdown Switch | Tickalara Duraqual Shipping Pump PF753 Panel Inst/Elec Service | 2644909.docx | 2644909 | 001
Pump-Plunger Duraqual PF753-135L65-TICK_A012 | Tickalara Satellite - Export - Shipping Pumps | Tickalara Satellite - Export - Shipping Pumps | 3800 - Tickalara Satellite | KICK EXP 3800-P-001B | KICK | EXP | 3800-P-001B | 12 | M | 01 | 00 | KICK EXP 12M-01-00 | KICK EXP 12M-01-00-002 | Overhaul Low Pump Oil Pressure Shutdown Switch | Tickalara Duraqual Shipping Pump PF753 Panel Inst/Elec Service | 2218083.docx | 2218083 | 002
Pump-Plunger Duraqual PF753-135L65-TICK_A012 | Tickalara Satellite - Export - Shipping Pumps | Tickalara Satellite - Export - Shipping Pumps | 3800 - Tickalara Satellite | KICK EXP 3800-P-001B | KICK | EXP | 3800-P-001B | 12 | M | 01 | 00 | KICK EXP 12M-01-00 | KICK EXP 12M-01-00-002 | Overhaul Low Engine Oil Pressure Shutdown Switch | Tickalara Duraqual Shipping Pump PF753 Panel Inst/Elec Service | 2218083.docx | 2218083 | 002
Pump-Plunger Duraqual PF753-135L65-TICK_A012 | Tickalara Satellite - Export - Shipping Pumps | Tickalara Satellite - Export - Shipping Pumps | 3800 - Tickalara Satellite | KICK EXP 3800-P-001B | KICK | EXP | 3800-P-001B | 6 | M | 04 | 00 | KICK EXP 6M-04-00 | KICK EXP 6M-04-00-001 | Check pulsation damper pre-charge pressure | Tickalara Duraqual Shipping Pump PF753-135L65 30 Weekly Mechanical Service | 2648683.DOCX | 2648683 | 001
Pump-Plunger Duraqual PF753-135L65-TICK_A012 | Tickalara Satellite - Export - Shipping Pumps | Tickalara Satellite - Export - Shipping Pumps | 3800 - Tickalara Satellite | KICK EXP 3800-P-001B | KICK | EXP | 3800-P-001B | 12 | M | 04 | 00 | KICK EXP 12M-04-00 | KICK EXP 12M-04-00-001 | Check pump foundation bolts are tight | Tickalara Duraqual Shipping Pump PF753-135L65 60 Weekly Mechanical Service | 2648707.docx | 2648707 | 001
Pump-Plunger Duraqual PF753-135L65-TICK_A012 | Tickalara Satellite - Export - Shipping Pumps | Tickalara Satellite - Export - Shipping Pumps | 3800 - Tickalara Satellite | KICK EXP 3800-P-001B | KICK | EXP | 3800-P-001B | 12 | M | 04 | 00 | KICK EXP 12M-04-00 | KICK EXP 12M-04-00-001 | Visually check pump pony rod for scoring | Tickalara Duraqual Shipping Pump PF753-135L65 60 Weekly Mechanical Service | 2648707.docx | 2648707 | 001
Pump-Plunger Duraqual PF753-135L65-TICK_A012 | Tickalara Satellite - Export - Shipping Pumps | Tickalara Satellite - Export - Shipping Pumps | 3800 - Tickalara Satellite | KICK EXP 3800-P-001B | KICK | EXP | 3800-P-001B | 6 | M | 04 | 00 | KICK EXP 6M-04-00 | KICK EXP 6M-04-00-001 | Check belt tension with belt tensioning tool | Tickalara Duraqual Shipping Pump PF753-135L65 30 Weekly Mechanical Service | 2648683.DOCX | 2648683 | 001
Pump-Plunger Duraqual PF753-135L65-TICK_A012 | Tickalara Satellite - Export - Shipping Pumps | Tickalara Satellite - Export - Shipping Pumps | 3800 - Tickalara Satellite | KICK EXP 3800-P-001B | KICK | EXP | 3800-P-001B | 12 | M | 04 | 00 | KICK EXP 12M-04-00 | KICK EXP 12M-04-00-001 | Replace pump drive belts and re-tension, Visually inspect condition of drive pulley grooves | Tickalara Duraqual Shipping Pump PF753-135L65 60 Weekly Mechanical Service | 2648707.docx | 2648707 | 001
Pump-Plunger Duraqual PF753-135L65-TICK_A012 | Tickalara Satellite - Export - Shipping Pumps | Tickalara Satellite - Export - Shipping Pumps | 3800 - Tickalara Satellite | KICK EXP 3800-P-001B | KICK | EXP | 3800-P-001B | 6 | M | 04 | 00 | KICK EXP 6M-04-00 | KICK EXP 6M-04-00-001 | Clean pump crankcase breather with a non-explosive solvent | Tickalara Duraqual Shipping Pump PF753-135L65 30 Weekly Mechanical Service | 2648683.DOCX | 2648683 | 001
Pump-Plunger Duraqual PF753-135L65-TICK_A012 | Tickalara Satellite - Export - Shipping Pumps | Tickalara Satellite - Export - Shipping Pumps | 3800 - Tickalara Satellite | KICK EXP 3800-P-001B | KICK | EXP | 3800-P-001B | 6 | M | 04 | 00 | KICK EXP 6M-04-00 | KICK EXP 6M-04-00-001 | Replace pump lube oil filter | Tickalara Duraqual Shipping Pump PF753-135L65 30 Weekly Mechanical Service | 2648683.DOCX | 2648683 | 001
Pump-Plunger Duraqual PF753-135L65-TICK_A012 | Tickalara Satellite - Export - Shipping Pumps | Tickalara Satellite - Export - Shipping Pumps | 3800 - Tickalara Satellite | KICK EXP 3800-P-001B | KICK | EXP | 3800-P-001B | 6 | M | 04 | 00 | KICK EXP 6M-04-00 | KICK EXP 6M-04-00-001 | Obtain oil sample from Plunger Pump | Tickalara Duraqual Shipping Pump PF753-135L65 30 Weekly Mechanical Service | 2648683.DOCX | 2648683 | 001
Pump-Plunger Duraqual PF753-135L65-TICK_A012 | Tickalara Satellite - Export - Shipping Pumps | Tickalara Satellite - Export - Shipping Pumps | 3800 - Tickalara Satellite | KICK EXP 3800-P-001A | KICK | EXP | 3800-P-001A | 12 | M | 04 | 00 | KICK EXP 12M-04-00 | KICK EXP 12M-04-00-001 | Check pump foundation bolts are tight | Tickalara Duraqual Shipping Pump PF753-135L65 60 Weekly Mechanical Service | 2648707.docx | 2648707 | 001
Pump-Plunger Duraqual PF753-135L65-TICK_A012 | Tickalara Satellite - Export - Shipping Pumps | Tickalara Satellite - Export - Shipping Pumps | 3800 - Tickalara Satellite | KICK EXP 3800-P-001A | KICK | EXP | 3800-P-001A | 6 | M | 04 | 00 | KICK EXP 6M-04-00 | KICK EXP 6M-04-00-001 | Replace pump lube oil filter | Tickalara Duraqual Shipping Pump PF753-135L65 30 Weekly Mechanical Service | 2648683.DOCX | 2648683 | 001
Pump-Plunger Duraqual PF753-135L65-TICK_A012 | Tickalara Satellite - Export - Shipping Pumps | Tickalara Satellite - Export - Shipping Pumps | 3800 - Tickalara Satellite | KICK EXP 3800-P-001A | KICK | EXP | 3800-P-001A | 6 | M | 04 | 00 | KICK EXP 6M-04-00 | KICK EXP 6M-04-00-001 | Obtain oil sample from Plunger Pump | Tickalara Duraqual Shipping Pump PF753-135L65 30 Weekly Mechanical Service | 2648683.DOCX | 2648683 | 001
Pump-Plunger Duraqual PF753-135L65-TICK_A012 | Tickalara Satellite - Export - Shipping Pumps | Tickalara Satellite - Export - Shipping Pumps | 3800 - Tickalara Satellite | KICK EXP 3800-P-001A | KICK | EXP | 3800-P-001A | 6 | M | 04 | 00 | KICK EXP 6M-04-00 | KICK EXP 6M-04-00-001 | Clean pump crankcase breather with a non-explosive solvent | Tickalara Duraqual Shipping Pump PF753-135L65 30 Weekly Mechanical Service | 2648683.DOCX | 2648683 | 001
Pump-Plunger Duraqual PF753-135L65-TICK_A012 | Tickalara Satellite - Export - Shipping Pumps | Tickalara Satellite - Export - Shipping Pumps | 3800 - Tickalara Satellite | KICK EXP 3800-P-001A | KICK | EXP | 3800-P-001A | 6 | M | 04 | 00 | KICK EXP 6M-04-00 | KICK EXP 6M-04-00-001 | Check belt tension with belt tensioning tool | Tickalara Duraqual Shipping Pump PF753-135L65 30 Weekly Mechanical Service | 2648683.DOCX | 2648683 | 001
Pump-Plunger Duraqual PF753-135L65-TICK_A012 | Tickalara Satellite - Export - Shipping Pumps | Tickalara Satellite - Export - Shipping Pumps | 3800 - Tickalara Satellite | KICK EXP 3800-P-001A | KICK | EXP | 3800-P-001A | 12 | M | 04 | 00 | KICK EXP 12M-04-00 | KICK EXP 12M-04-00-001 | Replace pump drive belts and re-tension, Visually inspect condition of drive pulley grooves | Tickalara Duraqual Shipping Pump PF753-135L65 60 Weekly Mechanical Service | 2648707.docx | 2648707 | 001
Pump-Plunger Duraqual PF753-135L65-TICK_A012 | Tickalara Satellite - Export - Shipping Pumps | Tickalara Satellite - Export - Shipping Pumps | 3800 - Tickalara Satellite | KICK EXP 3800-P-001A | KICK | EXP | 3800-P-001A | 12 | M | 04 | 00 | KICK EXP 12M-04-00 | KICK EXP 12M-04-00-001 | Visually check pump pony rod for scoring | Tickalara Duraqual Shipping Pump PF753-135L65 60 Weekly Mechanical Service | 2648707.docx | 2648707 | 001
Pump-Plunger Duraqual PF753-135L65-TICK_A012 | Tickalara Satellite - Export - Shipping Pumps | Tickalara Satellite - Export - Shipping Pumps | 3800 - Tickalara Satellite | KICK EXP 3800-P-001A | KICK | EXP | 3800-P-001A | 6 | M | 04 | 00 | KICK EXP 6M-04-00 | KICK EXP 6M-04-00-001 | Check pulsation damper pre-charge pressure | Tickalara Duraqual Shipping Pump PF753-135L65 30 Weekly Mechanical Service | 2648683.DOCX | 2648683 | 001
Pump-Plunger Duraqual PF753-135L65-TICK_A012 | Tickalara Satellite - Export - Shipping Pumps | Tickalara Satellite - Export - Shipping Pumps | 3800 - Tickalara Satellite | KICK EXP 3800-P-001A | KICK | EXP | 3800-P-001A | 12 | M | 01 | 00 | KICK EXP 12M-01-00 | KICK EXP 12M-01-00-002 | Overhaul Low Pump Oil Pressure Shutdown Switch | Tickalara Duraqual Shipping Pump PF753 Panel Inst/Elec Service | 2218083.docx | 2218083 | 002
Pump-Plunger Duraqual PF753-135L65-TICK_A012 | Tickalara Satellite - Export - Shipping Pumps | Tickalara Satellite - Export - Shipping Pumps | 3800 - Tickalara Satellite | KICK EXP 3800-P-001A | KICK | EXP | 3800-P-001A | 12 | M | 01 | 00 | KICK EXP 12M-01-00 | KICK EXP 12M-01-00-002 | Overhaul Low Engine Oil Pressure Shutdown Switch | Tickalara Duraqual Shipping Pump PF753 Panel Inst/Elec Service | 2218083.docx | 2218083 | 002
Pump-Plunger Duraqual PF753-135L65-TICK_A012 | Tickalara Satellite - Export - Shipping Pumps | Tickalara Satellite - Export - Shipping Pumps | 3800 - Tickalara Satellite | KICK EXP 3800-P-001A | KICK | EXP | 3800-P-001A | 12 | M | 01 | 00 | KICK EXP 12M-01-00 | KICK EXP 12M-01-00-001 | Overhaul Low Engine Water Flow Shutdown Switch | Tickalara Duraqual Shipping Pump PF753 Panel Inst/Elec Service | 2644909.docx | 2644909 | 001
Pump-Plunger Duraqual PF753-135L65-TICK_A012 | Tickalara Satellite - Export - Shipping Pumps | Tickalara Satellite - Export - Shipping Pumps | 3800 - Tickalara Satellite | KICK EXP 3800-P-001A | KICK | EXP | 3800-P-001A | 12 | M | 01 | 00 | KICK EXP 12M-01-00 | KICK EXP 12M-01-00-001 | Overhaul High Engine Oil Temperature Shutdown Switch | Tickalara Duraqual Shipping Pump PF753 Panel Inst/Elec Service | 2644909.docx | 2644909 | 001
Compressor-Air Champion CSI 7.5-TICK_A013 | Tickalara Satellite - Instrument Air - Air Compressor Package - 3800-KX-0003 | Tickalara Satellite - Instrument Air - Air Compressor Package - 3800-KX-0003 | 3800 - Tickalara Satellite | KICK INST AIR 3800-K-0003 | KICK | INST AIR | 3800-K-0003 | 12 | M | 04 | 00 | KICK INST AIR 12M-04-00 | KICK INST AIR 12M-04-00-001 | Check the condition of the inlet controller and service as required | Tickalara Champion CSI 7.5 Air Compressor Mechanical Service 1 Yearly | SERVICE-PM-CO.RE-900215-J-2007.docx | 2879279 | 001
Compressor-Air Champion CSI 7.5-TICK_A013 | Tickalara Satellite - Instrument Air - Air Compressor Package - 3800-KX-0003 | Tickalara Satellite - Instrument Air - Air Compressor Package - 3800-KX-0003 | 3800 - Tickalara Satellite | KICK INST AIR 3800-K-0003 | KICK | INST AIR | 3800-K-0003 | 6 | M | 04 | 00 | KICK INST AIR 6M-04-00 | KICK INST AIR 6M-04-00-001 | Check alignment of pulleys and adjust as required | Tickalara Champion CSI 7.5 Air Compressor Mechanical Service 6 Monthly | SERVICE-PM-CO.RE-900215-J-2006.docx | 2879278 | 001
Compressor-Air Champion CSI 7.5-TICK_A013 | Tickalara Satellite - Instrument Air - Air Compressor Package - 3800-KX-0003 | Tickalara Satellite - Instrument Air - Air Compressor Package - 3800-KX-0003 | 3800 - Tickalara Satellite | KICK INST AIR 3800-K-0003 | KICK | INST AIR | 3800-K-0003 | 6 | M | 04 | 00 | KICK INST AIR 6M-04-00 | KICK INST AIR 6M-04-00-001 | Check vee belt tension and adjust as necessary | Tickalara Champion CSI 7.5 Air Compressor Mechanical Service 6 Monthly | SERVICE-PM-CO.RE-900215-J-2006.docx | 2879278 | 001
Compressor-Air Champion CSI 7.5-TICK_A013 | Tickalara Satellite - Instrument Air - Air Compressor Package - 3800-KX-0003 | Tickalara Satellite - Instrument Air - Air Compressor Package - 3800-KX-0003 | 3800 - Tickalara Satellite | KICK INST AIR 3800-K-0003 | KICK | INST AIR | 3800-K-0003 | 6 | M | 04 | 00 | KICK INST AIR 6M-04-00 | KICK INST AIR 6M-04-00-001 | Check condition of vee belts and repalce if required | Tickalara Champion CSI 7.5 Air Compressor Mechanical Service 6 Monthly | SERVICE-PM-CO.RE-900215-J-2006.docx | 2879278 | 001
Compressor-Air Champion CSI 7.5-TICK_A013 | Tickalara Satellite - Instrument Air - Air Compressor Package - 3800-KX-0003 | Tickalara Satellite - Instrument Air - Air Compressor Package - 3800-KX-0003 | 3800 - Tickalara Satellite | KICK INST AIR 3800-K-0003 | KICK | INST AIR | 3800-K-0003 | 6 | M | 04 | 00 | KICK INST AIR 6M-04-00 | KICK INST AIR 6M-04-00-001 | Check all hold-down bolts and tighten as required | Tickalara Champion CSI 7.5 Air Compressor Mechanical Service 6 Monthly | SERVICE-PM-CO.RE-900215-J-2006.docx | 2879278 | 001
Compressor-Air Champion CSI 7.5-TICK_A013 | Tickalara Satellite - Instrument Air - Air Compressor Package - 3800-KX-0003 | Tickalara Satellite - Instrument Air - Air Compressor Package - 3800-KX-0003 | 3800 - Tickalara Satellite | KICK INST AIR 3800-K-0003 | KICK | INST AIR | 3800-K-0003 | 6 | M | 04 | 00 | KICK INST AIR 6M-04-00 | KICK INST AIR 6M-04-00-001 | Check all air lines and pipework for cracking or vibration damage | Tickalara Champion CSI 7.5 Air Compressor Mechanical Service 6 Monthly | SERVICE-PM-CO.RE-900215-J-2006.docx | 2879278 | 001
Compressor-Air Champion CSI 7.5-TICK_A013 | Tickalara Satellite - Instrument Air - Air Compressor Package - 3800-KX-0003 | Tickalara Satellite - Instrument Air - Air Compressor Package - 3800-KX-0003 | 3800 - Tickalara Satellite | KICK INST AIR 3800-K-0003 | KICK | INST AIR | 3800-K-0003 | 6 | M | 04 | 00 | KICK INST AIR 6M-04-00 | KICK INST AIR 6M-04-00-001 | Inspect all pipe work while running for any leakage and repair as needed | Tickalara Champion CSI 7.5 Air Compressor Mechanical Service 6 Monthly | SERVICE-PM-CO.RE-900215-J-2006.docx | 2879278 | 001
Compressor-Air Champion CSI 7.5-TICK_A013 | Tickalara Satellite - Instrument Air - Air Compressor Package - 3800-KX-0003 | Tickalara Satellite - Instrument Air - Air Compressor Package - 3800-KX-0003 | 3800 - Tickalara Satellite | KICK INST AIR 3800-K-0003 | KICK | INST AIR | 3800-K-0003 | 6 | M | 04 | 00 | KICK INST AIR 6M-04-00 | KICK INST AIR 6M-04-00-001 | Check the purge line sight glass for signs of flow | Tickalara Champion CSI 7.5 Air Compressor Mechanical Service 6 Monthly | SERVICE-PM-CO.RE-900215-J-2006.docx | 2879278 | 001
Compressor-Air Champion CSI 7.5-TICK_A013 | Tickalara Satellite - Instrument Air - Air Compressor Package - 3800-KX-0003 | Tickalara Satellite - Instrument Air - Air Compressor Package - 3800-KX-0003 | 3800 - Tickalara Satellite | KICK INST AIR 3800-K-0003 | KICK | INST AIR | 3800-K-0003 | 6 | M | 04 | 00 | KICK INST AIR 6M-04-00 | KICK INST AIR 6M-04-00-001 | Change the compressor oil | Tickalara Champion CSI 7.5 Air Compressor Mechanical Service 6 Monthly | SERVICE-PM-CO.RE-900215-J-2006.docx | 2879278 | 001
Compressor-Air Champion CSI 7.5-TICK_A013 | Tickalara Satellite - Instrument Air - Air Compressor Package - 3800-KX-0003 | Tickalara Satellite - Instrument Air - Air Compressor Package - 3800-KX-0003 | 3800 - Tickalara Satellite | KICK INST AIR 3800-K-0003 | KICK | INST AIR | 3800-K-0003 | 6 | M | 04 | 00 | KICK INST AIR 6M-04-00 | KICK INST AIR 6M-04-00-001 | Replace the oil filter element | Tickalara Champion CSI 7.5 Air Compressor Mechanical Service 6 Monthly | SERVICE-PM-CO.RE-900215-J-2006.docx | 2879278 | 001
Compressor-Air Champion CSI 7.5-TICK_A013 | Tickalara Satellite - Instrument Air - Air Compressor Package - 3800-KX-0003 | Tickalara Satellite - Instrument Air - Air Compressor Package - 3800-KX-0003 | 3800 - Tickalara Satellite | KICK INST AIR 3800-K-0003 | KICK | INST AIR | 3800-K-0003 | 6 | M | 04 | 00 | KICK INST AIR 6M-04-00 | KICK INST AIR 6M-04-00-001 | Drain liquids from all air receivers | Tickalara Champion CSI 7.5 Air Compressor Mechanical Service 6 Monthly | SERVICE-PM-CO.RE-900215-J-2006.docx | 2879278 | 001
Compressor-Air Champion CSI 7.5-TICK_A013 | Tickalara Satellite - Instrument Air - Air Compressor Package - 3800-KX-0003 | Tickalara Satellite - Instrument Air - Air Compressor Package - 3800-KX-0003 | 3800 - Tickalara Satellite | KICK INST AIR 3800-K-0003 | KICK | INST AIR | 3800-K-0003 | 12 | M | 04 | 00 | KICK INST AIR 12M-04-00 | KICK INST AIR 12M-04-00-001 | Check the condition of all safety devices and repair or replace as required | Tickalara Champion CSI 7.5 Air Compressor Mechanical Service 1 Yearly | SERVICE-PM-CO.RE-900215-J-2007.docx | 2879279 | 001
Compressor-Air Champion CSI 7.5-TICK_A013 | Tickalara Satellite - Instrument Air - Air Compressor Package - 3800-KX-0003 | Tickalara Satellite - Instrument Air - Air Compressor Package - 3800-KX-0003 | 3800 - Tickalara Satellite | KICK INST AIR 3800-K-0003 | KICK | INST AIR | 3800-K-0003 | 12 | M | 04 | 00 | KICK INST AIR 12M-04-00 | KICK INST AIR 12M-04-00-001 | Replace the seperator element | Tickalara Champion CSI 7.5 Air Compressor Mechanical Service 1 Yearly | SERVICE-PM-CO.RE-900215-J-2007.docx | 2879279 | 001
Compressor-Air Champion CSI 7.5-TICK_A013 | Tickalara Satellite - Instrument Air - Air Compressor Package - 3800-KX-0003 | Tickalara Satellite - Instrument Air - Air Compressor Package - 3800-KX-0003 | 3800 - Tickalara Satellite | KICK INST AIR 3800-K-0003 | KICK | INST AIR | 3800-K-0003 | 6 | M | 04 | 00 | KICK INST AIR 6M-04-00 | KICK INST AIR 6M-04-00-001 | Replace the air intake filter element | Tickalara Champion CSI 7.5 Air Compressor Mechanical Service 6 Monthly | SERVICE-PM-CO.RE-900215-J-2006.docx | 2879278 | 001
Compressor-Air Champion CSI 7.5-TICK_A013 | Tickalara Satellite - Instrument Air - Air Compressor Package - 3800-KX-0003 | Tickalara Satellite - Instrument Air - Air Compressor Package - 3800-KX-0003 | 3800 - Tickalara Satellite | KICK INST AIR 3800-K-0003 | KICK | INST AIR | 3800-K-0003 | 12 | M | 04 | 00 | KICK INST AIR 12M-04-00 | KICK INST AIR 12M-04-00-001 | Check the condition of the thermovalve and service as required | Tickalara Champion CSI 7.5 Air Compressor Mechanical Service 1 Yearly | SERVICE-PM-CO.RE-900215-J-2007.docx | 2879279 | 001
Compressor-Air Champion CSI 7.5-TICK_A013 | Tickalara Satellite - Instrument Air - Air Compressor Package - 3800-KX-0003 | Tickalara Satellite - Instrument Air - Air Compressor Package - 3800-KX-0003 | 3800 - Tickalara Satellite | KICK INST AIR 3800-K-0003 | KICK | INST AIR | 3800-K-0003 | 12 | M | 04 | 00 | KICK INST AIR 12M-04-00 | KICK INST AIR 12M-04-00-001 | Check the condition of the minimum pressure valve and service as required | Tickalara Champion CSI 7.5 Air Compressor Mechanical Service 1 Yearly | SERVICE-PM-CO.RE-900215-J-2007.docx | 2879279 | 001
Compressor-Air Champion APP10-TICK_A08 | Tickalara Satellite - Instrument Air - Air Compressor Package - 3800-KX-001 | Tickalara Satellite - Instrument Air - Air Compressor Package - 3800-KX-001 | 3800 - Tickalara Satellite | KICK INST AIR 3800-KX-001 | KICK | INST AIR | 3800-KX-001 | 6 | M | 04 | 00 | KICK INST AIR 6M-04-00 | KICK INST AIR 6M-04-00-002 | Check tightness of motor hold down bolts and compressor hold down bolts | Tickalara Champion APP10 Air Compressor Mechanical Service 6 Monthly | 2229263.docx | 2229263 | 002
Compressor-Air Champion APP10-TICK_A08 | Tickalara Satellite - Instrument Air - Air Compressor Package - 3800-KX-001 | Tickalara Satellite - Instrument Air - Air Compressor Package - 3800-KX-001 | 3800 - Tickalara Satellite | KICK INST AIR 3800-KX-001 | KICK | INST AIR | 3800-KX-001 | 12 | M | 04 | 00 | KICK INST AIR 12M-04-00 | KICK INST AIR 12M-04-00-002 | Replace v-belt set if required, adjust motor to achieve correct belt tension. Inspect pulley grooves for wear | Tickalara Champion APP10 Air Compressor Mechanical Service 1 Yearly | 2229618.docx | 2229618 | 002
Compressor-Air Champion APP10-TICK_A08 | Tickalara Satellite - Instrument Air - Air Compressor Package - 3800-KX-001 | Tickalara Satellite - Instrument Air - Air Compressor Package - 3800-KX-001 | 3800 - Tickalara Satellite | KICK INST AIR 3800-KX-001 | KICK | INST AIR | 3800-KX-001 | 6 | M | 04 | 00 | KICK INST AIR 6M-04-00 | KICK INST AIR 6M-04-00-002 | Check v-belt tension using belt tensioning tool, if adjustment required | Tickalara Champion APP10 Air Compressor Mechanical Service 6 Monthly | 2229263.docx | 2229263 | 002
Compressor-Air Champion APP10-TICK_A08 | Tickalara Satellite - Instrument Air - Air Compressor Package - 3800-KX-001 | Tickalara Satellite - Instrument Air - Air Compressor Package - 3800-KX-001 | 3800 - Tickalara Satellite | KICK INST AIR 3800-KX-001 | KICK | INST AIR | 3800-KX-001 | 3 | M | 04 | 00 | KICK INST AIR 3M-04-00 | KICK INST AIR 3M-04-00-001 | Clean filter housing of air intake filter, install new air filter | Tickalara Champion APP10 Air Compressor Mechanical Service 3 Monthly | 2232313.docx | 2232313 | 001
Compressor-Air Champion APP10-TICK_A08 | Tickalara Satellite - Instrument Air - Air Compressor Package - 3800-KX-001 | Tickalara Satellite - Instrument Air - Air Compressor Package - 3800-KX-001 | 3800 - Tickalara Satellite | KICK INST AIR 3800-KX-001 | KICK | INST AIR | 3800-KX-001 | 6 | M | 01 | 00 | KICK INST AIR 6M-01-00 | KICK INST AIR 6M-01-00-001 | Clean Condenser Fins | Tickalara Satellite 3800-KX-001 Instrument Air Compressor Package 1 Champion APP10 6 Monthly Instrument Service *Note-Ensure Backup Compressor Available To Be Put Online* | SERVICE-PM-PK.CO-900215-J-0159.docx | 2724098 | 001
Compressor-Air Champion APP10-TICK_A08 | Tickalara Satellite - Instrument Air - Air Compressor Package - 3800-KX-001 | Tickalara Satellite - Instrument Air - Air Compressor Package - 3800-KX-001 | 3800 - Tickalara Satellite | KICK INST AIR 3800-KX-001 | KICK | INST AIR | 3800-KX-001 | 6 | M | 04 | 00 | KICK INST AIR 6M-04-00 | KICK INST AIR 6M-04-00-002 | Clean compressor of dirt and oil with detergent and water | Tickalara Champion APP10 Air Compressor Mechanical Service 6 Monthly | 2229263.docx | 2229263 | 002
Compressor-Air Champion APP10-TICK_A08 | Tickalara Satellite - Instrument Air - Air Compressor Package - 3800-KX-001 | Tickalara Satellite - Instrument Air - Air Compressor Package - 3800-KX-001 | 3800 - Tickalara Satellite | KICK INST AIR 3800-KX-001 | KICK | INST AIR | 3800-KX-001 | 12 | M | 04 | 00 | KICK INST AIR 12M-04-00 | KICK INST AIR 12M-04-00-002 | Manually opearate lever or ring pull to activate receiver valve | Tickalara Champion APP10 Air Compressor Mechanical Service 1 Yearly | 2229618.docx | 2229618 | 002
Compressor-Air Champion APP10-TICK_A08 | Tickalara Satellite - Instrument Air - Air Compressor Package - 3800-KX-001 | Tickalara Satellite - Instrument Air - Air Compressor Package - 3800-KX-001 | 3800 - Tickalara Satellite | KICK INST AIR 3800-KX-001 | KICK | INST AIR | 3800-KX-001 | 6 | M | 04 | 00 | KICK INST AIR 6M-04-00 | KICK INST AIR 6M-04-00-002 | Clean carankcase air breather with non-explosive solvent | Tickalara Champion APP10 Air Compressor Mechanical Service 6 Monthly | 2229263.docx | 2229263 | 002
Compressor-Air Champion APP10-TICK_A08 | Tickalara Satellite - Instrument Air - Air Compressor Package - 3800-KX-001 | Tickalara Satellite - Instrument Air - Air Compressor Package - 3800-KX-001 | 3800 - Tickalara Satellite | KICK INST AIR 3800-KX-001 | KICK | INST AIR | 3800-KX-001 | 3 | M | 04 | 00 | KICK INST AIR 3M-04-00 | KICK INST AIR 3M-04-00-001 | Test condition of compressor oil, replace oil sight glass | Tickalara Champion APP10 Air Compressor Mechanical Service 3 Monthly | 2232313.docx | 2232313 | 001
Compressor-Air Champion APP10-TICK_A08 | Tickalara Satellite - Instrument Air - Air Compressor Package - 3800-KX-001 | Tickalara Satellite - Instrument Air - Air Compressor Package - 3800-KX-001 | 3800 - Tickalara Satellite | KICK INST AIR 3800-KX-001 | KICK | INST AIR | 3800-KX-001 | 6 | M | 04 | 00 | KICK INST AIR 6M-04-00 | KICK INST AIR 6M-04-00-002 | Drain compressor crankcase oil, if oil change required.Visually inspect oil for metal particles | Tickalara Champion APP10 Air Compressor Mechanical Service 6 Monthly | 2229263.docx | 2229263 | 002
Compressor-Air Champion APP10-TICK_A08 | Tickalara Satellite - Instrument Air - Air Compressor Package - 3800-KX-001 | Tickalara Satellite - Instrument Air - Air Compressor Package - 3800-KX-001 | 3800 - Tickalara Satellite | KICK INST AIR 3800-KX-001 | KICK | INST AIR | 3800-KX-001 | 6 | M | 04 | 00 | KICK INST AIR 6M-04-00 | KICK INST AIR 6M-04-00-002 | Visually inspect compressor for oil leaks | Tickalara Champion APP10 Air Compressor Mechanical Service 6 Monthly | 2229263.docx | 2229263 | 002
Compressor-Air Champion APP10-TICK_A08 | Tickalara Satellite - Instrument Air - Air Compressor Package - 3800-KX-001 | Tickalara Satellite - Instrument Air - Air Compressor Package - 3800-KX-001 | 3800 - Tickalara Satellite | KICK INST AIR 3800-KX-001 | KICK | INST AIR | 3800-KX-001 | 12 | M | 01 | 00 | KICK INST AIR 12M-01-00 | KICK INST AIR 12M-01-00-001 | Visually inspect motor terminal box terminal box gasket for deterioration and terminal box contamination | Tickalara Satellite 3800-KX-001 Instrument Air Compressor Package 1Champion APP10 Annual Instrument Service | 2218923.docx | 2218923 | 001
Compressor-Air Champion APP10-TICK_A08 | Tickalara Satellite - Instrument Air - Air Compressor Package - 3800-KX-001 | Tickalara Satellite - Instrument Air - Air Compressor Package - 3800-KX-001 | 3800 - Tickalara Satellite | KICK INST AIR 3800-KX-001 | KICK | INST AIR | 3800-KX-001 | 12 | M | 01 | 00 | KICK INST AIR 12M-01-00 | KICK INST AIR 12M-01-00-001 | Check tightness of local earth wiring connections, visually inspect condition of all earth wiring for deterioration | Tickalara Satellite 3800-KX-001 Instrument Air Compressor Package 1Champion APP10 Annual Instrument Service | 2218923.docx | 2218923 | 001
Compressor-Air Champion APP10-TICK_A08 | Tickalara Satellite - Instrument Air - Air Compressor Package - 3800-KX-001 | Tickalara Satellite - Instrument Air - Air Compressor Package - 3800-KX-001 | 3800 - Tickalara Satellite | KICK INST AIR 3800-KX-001 | KICK | INST AIR | 3800-KX-001 | 12 | M | 01 | 00 | KICK INST AIR 12M-01-00 | KICK INST AIR 12M-01-00-001 | Visually inspect wiring and cable gland for evidence of rubbing and deterioration, check calibration of high water temperature switch | Tickalara Satellite 3800-KX-001 Instrument Air Compressor Package 1Champion APP10 Annual Instrument Service | 2218923.docx | 2218923 | 001
Compressor-Air Champion APP10-TICK_A08 | Tickalara Satellite - Instrument Air - Air Compressor Package - 3800-KX-001 | Tickalara Satellite - Instrument Air - Air Compressor Package - 3800-KX-001 | 3800 - Tickalara Satellite | KICK INST AIR 3800-KX-001 | KICK | INST AIR | 3800-KX-001 | 12 | M | 01 | 00 | KICK INST AIR 12M-01-00 | KICK INST AIR 12M-01-00-001 | Visually inspect wiring and cable gland for evidence of rubbing and deterioration, check calibration of low oil pressure switch | Tickalara Satellite 3800-KX-001 Instrument Air Compressor Package 1Champion APP10 Annual Instrument Service | 2218923.docx | 2218923 | 001
Compressor-Air Champion APP10-TICK_A08 | Tickalara Satellite - Instrument Air - Air Compressor Package - 3800-KX-001 | Tickalara Satellite - Instrument Air - Air Compressor Package - 3800-KX-001 | 3800 - Tickalara Satellite | KICK INST AIR 3800-KX-001 | KICK | INST AIR | 3800-KX-001 | 12 | M | 01 | 00 | KICK INST AIR 12M-01-00 | KICK INST AIR 12M-01-00-001 | Visually inspect wiring and cable gland for evidence of rubbing and deterioration, check calibration of high discharge air temperature switch | Tickalara Satellite 3800-KX-001 Instrument Air Compressor Package 1Champion APP10 Annual Instrument Service | 2218923.docx | 2218923 | 001
Compressor-Air Champion APP10-TICK_A08 | Tickalara Satellite - Instrument Air - Air Compressor Package - 3800-KX-001 | Tickalara Satellite - Instrument Air - Air Compressor Package - 3800-KX-001 | 3800 - Tickalara Satellite | KICK INST AIR 3800-KX-001 | KICK | INST AIR | 3800-KX-001 | 12 | M | 01 | 00 | KICK INST AIR 12M-01-00 | KICK INST AIR 12M-01-00-001 | Visually inspect condition of 3 phase and control cables and lugs for deteriorations, overheating and support in terminal box | Tickalara Satellite 3800-KX-001 Instrument Air Compressor Package 1Champion APP10 Annual Instrument Service | 2218923.docx | 2218923 | 001
Compressor-Air Champion APP10-TICK_A08 | Tickalara Satellite - Instrument Air - Air Compressor Package - 3800-KX-001 | Tickalara Satellite - Instrument Air - Air Compressor Package - 3800-KX-001 | 3800 - Tickalara Satellite | KICK INST AIR 3800-KX-001 | KICK | INST AIR | 3800-KX-001 | 12 | M | 01 | 00 | KICK INST AIR 12M-01-00 | KICK INST AIR 12M-01-00-001 | Visually inspect wiring and cable gland for evidence of rubbing and deterioration, check calibration of low suction pressure switch | Tickalara Satellite 3800-KX-001 Instrument Air Compressor Package 1Champion APP10 Annual Instrument Service | 2218923.docx | 2218923 | 001
Compressor-Air Champion APP10-TICK_A08 | Tickalara Satellite - Instrument Air - Air Compressor Package - 3800-KX-001 | Tickalara Satellite - Instrument Air - Air Compressor Package - 3800-KX-001 | 3800 - Tickalara Satellite | KICK INST AIR 3800-KX-001 | KICK | INST AIR | 3800-KX-001 | 12 | M | 01 | 00 | KICK INST AIR 12M-01-00 | KICK INST AIR 12M-01-00-001 | Visually inspect control panel wiring for evidence of overheating | Tickalara Satellite 3800-KX-001 Instrument Air Compressor Package 1Champion APP10 Annual Instrument Service | 2218923.docx | 2218923 | 001
Compressor-Air Champion APP10-TICK_A013 | Tickalara Satellite - Instrument Air - Air Compressor Package - 3800-KX-001 | Tickalara Satellite - Instrument Air - Air Compressor Package - 3800-KX-001 | 3800 - Tickalara Satellite | KICK INST AIR 3800-K-001 | KICK | INST AIR | 3800-K-001 | 12 | M | 01 | 00 | KICK INST AIR 12M-01-00 | KICK INST AIR 12M-01-00-001 | Visually inspect wiring and cable gland for evidence of rubbing and deterioration, check calibration of high discharge air temperature switch | Tickalara Satellite 3800-KX-001 Instrument Air Compressor Package 1Champion APP10 Annual Instrument Service | 2218923.docx | 2218923 | 001
Compressor-Air Champion APP10-TICK_A013 | Tickalara Satellite - Instrument Air - Air Compressor Package - 3800-KX-001 | Tickalara Satellite - Instrument Air - Air Compressor Package - 3800-KX-001 | 3800 - Tickalara Satellite | KICK INST AIR 3800-K-001 | KICK | INST AIR | 3800-K-001 | 12 | M | 01 | 00 | KICK INST AIR 12M-01-00 | KICK INST AIR 12M-01-00-001 | Visually inspect condition of 3 phase and control cables and lugs for deteriorations, overheating and support in terminal box | Tickalara Satellite 3800-KX-001 Instrument Air Compressor Package 1Champion APP10 Annual Instrument Service | 2218923.docx | 2218923 | 001
Compressor-Air Champion APP10-TICK_A013 | Tickalara Satellite - Instrument Air - Air Compressor Package - 3800-KX-001 | Tickalara Satellite - Instrument Air - Air Compressor Package - 3800-KX-001 | 3800 - Tickalara Satellite | KICK INST AIR 3800-K-001 | KICK | INST AIR | 3800-K-001 | 12 | M | 01 | 00 | KICK INST AIR 12M-01-00 | KICK INST AIR 12M-01-00-001 | Visually inspect wiring and cable gland for evidence of rubbing and deterioration, check calibration of low oil pressure switch | Tickalara Satellite 3800-KX-001 Instrument Air Compressor Package 1Champion APP10 Annual Instrument Service | 2218923.docx | 2218923 | 001
Compressor-Air Champion APP10-TICK_A013 | Tickalara Satellite - Instrument Air - Air Compressor Package - 3800-KX-001 | Tickalara Satellite - Instrument Air - Air Compressor Package - 3800-KX-001 | 3800 - Tickalara Satellite | KICK INST AIR 3800-K-001 | KICK | INST AIR | 3800-K-001 | 12 | M | 01 | 00 | KICK INST AIR 12M-01-00 | KICK INST AIR 12M-01-00-001 | Visually inspect wiring and cable gland for evidence of rubbing and deterioration, check calibration of high water temperature switch | Tickalara Satellite 3800-KX-001 Instrument Air Compressor Package 1Champion APP10 Annual Instrument Service | 2218923.docx | 2218923 | 001
Compressor-Air Champion APP10-TICK_A013 | Tickalara Satellite - Instrument Air - Air Compressor Package - 3800-KX-001 | Tickalara Satellite - Instrument Air - Air Compressor Package - 3800-KX-001 | 3800 - Tickalara Satellite | KICK INST AIR 3800-K-001 | KICK | INST AIR | 3800-K-001 | 12 | M | 01 | 00 | KICK INST AIR 12M-01-00 | KICK INST AIR 12M-01-00-001 | Visually inspect wiring and cable gland for evidence of rubbing and deterioration, check calibration of low suction pressure switch | Tickalara Satellite 3800-KX-001 Instrument Air Compressor Package 1Champion APP10 Annual Instrument Service | 2218923.docx | 2218923 | 001
Compressor-Air Champion APP10-TICK_A013 | Tickalara Satellite - Instrument Air - Air Compressor Package - 3800-KX-001 | Tickalara Satellite - Instrument Air - Air Compressor Package - 3800-KX-001 | 3800 - Tickalara Satellite | KICK INST AIR 3800-K-001 | KICK | INST AIR | 3800-K-001 | 12 | M | 01 | 00 | KICK INST AIR 12M-01-00 | KICK INST AIR 12M-01-00-001 | Visually inspect control panel wiring for evidence of overheating | Tickalara Satellite 3800-KX-001 Instrument Air Compressor Package 1Champion APP10 Annual Instrument Service | 2218923.docx | 2218923 | 001
Compressor-Air Champion APP10-TICK_A013 | Tickalara Satellite - Instrument Air - Air Compressor Package - 3800-KX-001 | Tickalara Satellite - Instrument Air - Air Compressor Package - 3800-KX-001 | 3800 - Tickalara Satellite | KICK INST AIR 3800-K-001 | KICK | INST AIR | 3800-K-001 | 6 | M | 04 | 00 | KICK INST AIR 6M-04-00 | KICK INST AIR 6M-04-00-002 | Drain compressor crankcase oil, if oil change required.Visually inspect oil for metal particles | Tickalara Champion APP10 Air Compressor Mechanical Service 6 Monthly | 2229263.docx | 2229263 | 002
Compressor-Air Champion APP10-TICK_A013 | Tickalara Satellite - Instrument Air - Air Compressor Package - 3800-KX-001 | Tickalara Satellite - Instrument Air - Air Compressor Package - 3800-KX-001 | 3800 - Tickalara Satellite | KICK INST AIR 3800-K-001 | KICK | INST AIR | 3800-K-001 | 3 | M | 04 | 00 | KICK INST AIR 3M-04-00 | KICK INST AIR 3M-04-00-001 | Test condition of compressor oil, replace oil sight glass | Tickalara Champion APP10 Air Compressor Mechanical Service 3 Monthly | 2232313.docx | 2232313 | 001
Compressor-Air Champion APP10-TICK_A013 | Tickalara Satellite - Instrument Air - Air Compressor Package - 3800-KX-001 | Tickalara Satellite - Instrument Air - Air Compressor Package - 3800-KX-001 | 3800 - Tickalara Satellite | KICK INST AIR 3800-K-001 | KICK | INST AIR | 3800-K-001 | 6 | M | 04 | 00 | KICK INST AIR 6M-04-00 | KICK INST AIR 6M-04-00-002 | Visually inspect compressor for oil leaks | Tickalara Champion APP10 Air Compressor Mechanical Service 6 Monthly | 2229263.docx | 2229263 | 002
Compressor-Air Champion APP10-TICK_A013 | Tickalara Satellite - Instrument Air - Air Compressor Package - 3800-KX-001 | Tickalara Satellite - Instrument Air - Air Compressor Package - 3800-KX-001 | 3800 - Tickalara Satellite | KICK INST AIR 3800-K-001 | KICK | INST AIR | 3800-K-001 | 6 | M | 04 | 00 | KICK INST AIR 6M-04-00 | KICK INST AIR 6M-04-00-002 | Clean carankcase air breather with non-explosive solvent | Tickalara Champion APP10 Air Compressor Mechanical Service 6 Monthly | 2229263.docx | 2229263 | 002
Compressor-Air Champion APP10-TICK_A013 | Tickalara Satellite - Instrument Air - Air Compressor Package - 3800-KX-001 | Tickalara Satellite - Instrument Air - Air Compressor Package - 3800-KX-001 | 3800 - Tickalara Satellite | KICK INST AIR 3800-K-001 | KICK | INST AIR | 3800-K-001 | 6 | M | 04 | 00 | KICK INST AIR 6M-04-00 | KICK INST AIR 6M-04-00-002 | Clean compressor of dirt and oil with detergent and water | Tickalara Champion APP10 Air Compressor Mechanical Service 6 Monthly | 2229263.docx | 2229263 | 002
Compressor-Air Champion APP10-TICK_A013 | Tickalara Satellite - Instrument Air - Air Compressor Package - 3800-KX-001 | Tickalara Satellite - Instrument Air - Air Compressor Package - 3800-KX-001 | 3800 - Tickalara Satellite | KICK INST AIR 3800-K-001 | KICK | INST AIR | 3800-K-001 | 6 | M | 01 | 00 | KICK INST AIR 6M-01-00 | KICK INST AIR 6M-01-00-001 | Clean Condenser Fins | Tickalara Satellite 3800-KX-001 Instrument Air Compressor Package 1 Champion APP10 6 Monthly Instrument Service *Note-Ensure Backup Compressor Available To Be Put Online* | SERVICE-PM-PK.CO-900215-J-0159.docx | 2724098 | 001
Compressor-Air Champion APP10-TICK_A013 | Tickalara Satellite - Instrument Air - Air Compressor Package - 3800-KX-001 | Tickalara Satellite - Instrument Air - Air Compressor Package - 3800-KX-001 | 3800 - Tickalara Satellite | KICK INST AIR 3800-K-001 | KICK | INST AIR | 3800-K-001 | 12 | M | 04 | 00 | KICK INST AIR 12M-04-00 | KICK INST AIR 12M-04-00-002 | Manually opearate lever or ring pull to activate receiver valve | Tickalara Champion APP10 Air Compressor Mechanical Service 1 Yearly | 2229618.docx | 2229618 | 002
Compressor-Air Champion APP10-TICK_A013 | Tickalara Satellite - Instrument Air - Air Compressor Package - 3800-KX-001 | Tickalara Satellite - Instrument Air - Air Compressor Package - 3800-KX-001 | 3800 - Tickalara Satellite | KICK INST AIR 3800-K-001 | KICK | INST AIR | 3800-K-001 | 3 | M | 04 | 00 | KICK INST AIR 3M-04-00 | KICK INST AIR 3M-04-00-001 | Clean filter housing of air intake filter, install new air filter | Tickalara Champion APP10 Air Compressor Mechanical Service 3 Monthly | 2232313.docx | 2232313 | 001
Compressor-Air Champion APP10-TICK_A013 | Tickalara Satellite - Instrument Air - Air Compressor Package - 3800-KX-001 | Tickalara Satellite - Instrument Air - Air Compressor Package - 3800-KX-001 | 3800 - Tickalara Satellite | KICK INST AIR 3800-K-001 | KICK | INST AIR | 3800-K-001 | 12 | M | 04 | 00 | KICK INST AIR 12M-04-00 | KICK INST AIR 12M-04-00-002 | Replace v-belt set if required, adjust motor to achieve correct belt tension. Inspect pulley grooves for wear | Tickalara Champion APP10 Air Compressor Mechanical Service 1 Yearly | 2229618.docx | 2229618 | 002
Compressor-Air Champion APP10-TICK_A013 | Tickalara Satellite - Instrument Air - Air Compressor Package - 3800-KX-001 | Tickalara Satellite - Instrument Air - Air Compressor Package - 3800-KX-001 | 3800 - Tickalara Satellite | KICK INST AIR 3800-K-001 | KICK | INST AIR | 3800-K-001 | 6 | M | 04 | 00 | KICK INST AIR 6M-04-00 | KICK INST AIR 6M-04-00-002 | Check v-belt tension using belt tensioning tool, if adjustment required | Tickalara Champion APP10 Air Compressor Mechanical Service 6 Monthly | 2229263.docx | 2229263 | 002
Compressor-Air Champion APP10-TICK_A013 | Tickalara Satellite - Instrument Air - Air Compressor Package - 3800-KX-001 | Tickalara Satellite - Instrument Air - Air Compressor Package - 3800-KX-001 | 3800 - Tickalara Satellite | KICK INST AIR 3800-K-001 | KICK | INST AIR | 3800-K-001 | 6 | M | 04 | 00 | KICK INST AIR 6M-04-00 | KICK INST AIR 6M-04-00-002 | Check tightness of motor hold down bolts and compressor hold down bolts | Tickalara Champion APP10 Air Compressor Mechanical Service 6 Monthly | 2229263.docx | 2229263 | 002
Compressor-Air Champion APP10-TICK_A013 | Tickalara Satellite - Instrument Air - Air Compressor Package - 3800-KX-001 | Tickalara Satellite - Instrument Air - Air Compressor Package - 3800-KX-001 | 3800 - Tickalara Satellite | KICK INST AIR 3800-K-001 | KICK | INST AIR | 3800-K-001 | 12 | M | 01 | 00 | KICK INST AIR 12M-01-00 | KICK INST AIR 12M-01-00-001 | Visually inspect motor terminal box terminal box gasket for deterioration and terminal box contamination | Tickalara Satellite 3800-KX-001 Instrument Air Compressor Package 1Champion APP10 Annual Instrument Service | 2218923.docx | 2218923 | 001
Compressor-Air Champion APP10-TICK_A013 | Tickalara Satellite - Instrument Air - Air Compressor Package - 3800-KX-001 | Tickalara Satellite - Instrument Air - Air Compressor Package - 3800-KX-001 | 3800 - Tickalara Satellite | KICK INST AIR 3800-K-001 | KICK | INST AIR | 3800-K-001 | 12 | M | 01 | 00 | KICK INST AIR 12M-01-00 | KICK INST AIR 12M-01-00-001 | Check tightness of local earth wiring connections, visually inspect condition of all earth wiring for deterioration | Tickalara Satellite 3800-KX-001 Instrument Air Compressor Package 1Champion APP10 Annual Instrument Service | 2218923.docx | 2218923 | 001
Compressor-Air Atlas Copco XAS 36YD-TICK_A23 | Tickalara Satellite - Instrument Air - Air Compressor Package - 3800-KX-002 | Tickalara Satellite - Instrument Air - Air Compressor Package - 3800-KX-002 | 3800 - Tickalara Satellite | KICK INST AIR 3800-KX-002 | KICK | INST AIR | 3800-KX-002 | 60 | W | 01 | 00 | KICK INST AIR 60W-01-00 | KICK INST AIR 60W-01-00-001 | Check condition and tighteness of all terminations, including earth connections | Tickalara Atlas Copco Air Compressor XAS 36YD Inst/Elec Service | 2257107.docx | 2257107 | 001
Compressor-Air Atlas Copco XAS 36YD-TICK_A23 | Tickalara Satellite - Instrument Air - Air Compressor Package - 3800-KX-002 | Tickalara Satellite - Instrument Air - Air Compressor Package - 3800-KX-002 | 3800 - Tickalara Satellite | KICK INST AIR 3800-KX-002 | KICK | INST AIR | 3800-KX-002 | 10 | W | 04 | 00 | KICK INST AIR 10W-04-00 | KICK INST AIR 10W-04-00-001 | Adjust cylinder head valve clearances | Tickalara Atlas Copco Air Compressor XAS 36YD 10 Weekly Mechanical Service | 2245887.docx | 2245887 | 001
Compressor-Air Atlas Copco XAS 36YD-TICK_A23 | Tickalara Satellite - Instrument Air - Air Compressor Package - 3800-KX-002 | Tickalara Satellite - Instrument Air - Air Compressor Package - 3800-KX-002 | 3800 - Tickalara Satellite | KICK INST AIR 3800-KX-002 | KICK | INST AIR | 3800-KX-002 | 40 | W | 04 | 00 | KICK INST AIR 40W-04-00 | KICK INST AIR 40W-04-00-001 | Clean out loose dust from filter housing of intake filter element | Tickalara Atlas Copco Air Compressor XAS 36YD 40 Weekly Mechanical Service | 2246636.docx | 2246636 | 001
Compressor-Air Atlas Copco XAS 36YD-TICK_A23 | Tickalara Satellite - Instrument Air - Air Compressor Package - 3800-KX-002 | Tickalara Satellite - Instrument Air - Air Compressor Package - 3800-KX-002 | 3800 - Tickalara Satellite | KICK INST AIR 3800-KX-002 | KICK | INST AIR | 3800-KX-002 | 40 | W | 04 | 00 | KICK INST AIR 40W-04-00 | KICK INST AIR 40W-04-00-001 | Inspect loading plunger and unloader valve, replace loading plunger diaphragm and unloader seals | Tickalara Atlas Copco Air Compressor XAS 36YD 40 Weekly Mechanical Service | 2246636.docx | 2246636 | 001
Compressor-Air Atlas Copco XAS 36YD-TICK_A23 | Tickalara Satellite - Instrument Air - Air Compressor Package - 3800-KX-002 | Tickalara Satellite - Instrument Air - Air Compressor Package - 3800-KX-002 | 3800 - Tickalara Satellite | KICK INST AIR 3800-KX-002 | KICK | INST AIR | 3800-KX-002 | 5 | W | 04 | 00 | KICK INST AIR 5W-04-00 | KICK INST AIR 5W-04-00-001 | Replace engine oil filter | Tickalara Atlas Copco Air Compressor XAS 36YD Mechanical service 5 Weekly | 2245805.DOCX | 2245805 | 001
Compressor-Air Atlas Copco XAS 36YD-TICK_A23 | Tickalara Satellite - Instrument Air - Air Compressor Package - 3800-KX-002 | Tickalara Satellite - Instrument Air - Air Compressor Package - 3800-KX-002 | 3800 - Tickalara Satellite | KICK INST AIR 3800-KX-002 | KICK | INST AIR | 3800-KX-002 | 5 | W | 04 | 00 | KICK INST AIR 5W-04-00 | KICK INST AIR 5W-04-00-001 | Drain oil engine, close engine drain valve and replace engine drain plug. Inspect engine for visible oil leak | Tickalara Atlas Copco Air Compressor XAS 36YD Mechanical service 5 Weekly | 2245805.DOCX | 2245805 | 001
Compressor-Air Atlas Copco XAS 36YD-TICK_A23 | Tickalara Satellite - Instrument Air - Air Compressor Package - 3800-KX-002 | Tickalara Satellite - Instrument Air - Air Compressor Package - 3800-KX-002 | 3800 - Tickalara Satellite | KICK INST AIR 3800-KX-002 | KICK | INST AIR | 3800-KX-002 | 10 | W | 04 | 00 | KICK INST AIR 10W-04-00 | KICK INST AIR 10W-04-00-001 | Replace lube oil filters | Tickalara Atlas Copco Air Compressor XAS 36YD 10 Weekly Mechanical Service | 2245887.docx | 2245887 | 001
Compressor-Air Atlas Copco XAS 36YD-TICK_A23 | Tickalara Satellite - Instrument Air - Air Compressor Package - 3800-KX-002 | Tickalara Satellite - Instrument Air - Air Compressor Package - 3800-KX-002 | 3800 - Tickalara Satellite | KICK INST AIR 3800-KX-002 | KICK | INST AIR | 3800-KX-002 | 60 | W | 01 | 00 | KICK INST AIR 60W-01-00 | KICK INST AIR 60W-01-00-001 | Obtain oil sample from engine | Tickalara Atlas Copco Air Compressor XAS 36YD Inst/Elec Service | 2257107.docx | 2257107 | 001
Compressor-Air Atlas Copco XAS 36YD-TICK_A23 | Tickalara Satellite - Instrument Air - Air Compressor Package - 3800-KX-002 | Tickalara Satellite - Instrument Air - Air Compressor Package - 3800-KX-002 | 3800 - Tickalara Satellite | KICK INST AIR 3800-KX-002 | KICK | INST AIR | 3800-KX-002 | 40 | W | 04 | 00 | KICK INST AIR 40W-04-00 | KICK INST AIR 40W-04-00-001 | Clean coupling and visually inspect flexible insert for wear and cracking, check tightness of coupling bolts | Tickalara Atlas Copco Air Compressor XAS 36YD 40 Weekly Mechanical Service | 2246636.docx | 2246636 | 001
Compressor-Air Atlas Copco XAS 36YD-TICK_A23 | Tickalara Satellite - Instrument Air - Air Compressor Package - 3800-KX-002 | Tickalara Satellite - Instrument Air - Air Compressor Package - 3800-KX-002 | 3800 - Tickalara Satellite | KICK INST AIR 3800-KX-002 | KICK | INST AIR | 3800-KX-002 | 60 | W | 01 | 00 | KICK INST AIR 60W-01-00 | KICK INST AIR 60W-01-00-001 | Visually inspect gasket for deterioration and terminal box for contamination | Tickalara Atlas Copco Air Compressor XAS 36YD Inst/Elec Service | 2257107.docx | 2257107 | 001
Compressor-Air Atlas Copco XAS 36YD-TICK_A23 | Tickalara Satellite - Instrument Air - Air Compressor Package - 3800-KX-002 | Tickalara Satellite - Instrument Air - Air Compressor Package - 3800-KX-002 | 3800 - Tickalara Satellite | KICK INST AIR 3800-KX-002 | KICK | INST AIR | 3800-KX-002 | 40 | W | 04 | 00 | KICK INST AIR 40W-04-00 | KICK INST AIR 40W-04-00-001 | Clean external fins on oil cooler and after cooler with de-greaser and pressure water | Tickalara Atlas Copco Air Compressor XAS 36YD 40 Weekly Mechanical Service | 2246636.docx | 2246636 | 001
Compressor-Air Atlas Copco XAS 36YD-TICK_A23 | Tickalara Satellite - Instrument Air - Air Compressor Package - 3800-KX-002 | Tickalara Satellite - Instrument Air - Air Compressor Package - 3800-KX-002 | 3800 - Tickalara Satellite | KICK INST AIR 3800-KX-002 | KICK | INST AIR | 3800-KX-002 | 5 | W | 04 | 00 | KICK INST AIR 5W-04-00 | KICK INST AIR 5W-04-00-001 | Clean air pre-cleaner dust bowl, visually inspect dust bowl for cracks | Tickalara Atlas Copco Air Compressor XAS 36YD Mechanical service 5 Weekly | 2245805.DOCX | 2245805 | 001
Compressor-Air Atlas Copco XAS 36YD-TICK_A23 | Tickalara Satellite - Instrument Air - Air Compressor Package - 3800-KX-002 | Tickalara Satellite - Instrument Air - Air Compressor Package - 3800-KX-002 | 3800 - Tickalara Satellite | KICK INST AIR 3800-KX-002 | KICK | INST AIR | 3800-KX-002 | 10 | W | 04 | 00 | KICK INST AIR 10W-04-00 | KICK INST AIR 10W-04-00-001 | Replace fuel filter | Tickalara Atlas Copco Air Compressor XAS 36YD 10 Weekly Mechanical Service | 2245887.docx | 2245887 | 001
Compressor-Air Atlas Copco XAS 36YD-TICK_A23 | Tickalara Satellite - Instrument Air - Air Compressor Package - 3800-KX-002 | Tickalara Satellite - Instrument Air - Air Compressor Package - 3800-KX-002 | 3800 - Tickalara Satellite | KICK INST AIR 3800-KX-002 | KICK | INST AIR | 3800-KX-002 | 5 | W | 04 | 00 | KICK INST AIR 5W-04-00 | KICK INST AIR 5W-04-00-001 | Visually inspect governor linkages for excess free play and lubricate | Tickalara Atlas Copco Air Compressor XAS 36YD Mechanical service 5 Weekly | 2245805.DOCX | 2245805 | 001
Compressor-Air Atlas Copco XAS 36YD-TICK_A23 | Tickalara Satellite - Instrument Air - Air Compressor Package - 3800-KX-002 | Tickalara Satellite - Instrument Air - Air Compressor Package - 3800-KX-002 | 3800 - Tickalara Satellite | KICK INST AIR 3800-KX-002 | KICK | INST AIR | 3800-KX-002 | 5 | W | 04 | 00 | KICK INST AIR 5W-04-00 | KICK INST AIR 5W-04-00-001 | Clean housing and install new air intake filter element | Tickalara Atlas Copco Air Compressor XAS 36YD Mechanical service 5 Weekly | 2245805.DOCX | 2245805 | 001
Compressor-Air Atlas Copco XAS 36YD-TICK_A23 | Tickalara Satellite - Instrument Air - Air Compressor Package - 3800-KX-002 | Tickalara Satellite - Instrument Air - Air Compressor Package - 3800-KX-002 | 3800 - Tickalara Satellite | KICK INST AIR 3800-KX-002 | KICK | INST AIR | 3800-KX-002 | 40 | W | 04 | 00 | KICK INST AIR 40W-04-00 | KICK INST AIR 40W-04-00-001 | Visually inspect all belt pulleys for groove wear and bearing play | Tickalara Atlas Copco Air Compressor XAS 36YD 40 Weekly Mechanical Service | 2246636.docx | 2246636 | 001
Compressor-Air Atlas Copco XAS 36YD-TICK_A23 | Tickalara Satellite - Instrument Air - Air Compressor Package - 3800-KX-002 | Tickalara Satellite - Instrument Air - Air Compressor Package - 3800-KX-002 | 3800 - Tickalara Satellite | KICK INST AIR 3800-KX-002 | KICK | INST AIR | 3800-KX-002 | 40 | W | 04 | 00 | KICK INST AIR 40W-04-00 | KICK INST AIR 40W-04-00-001 | Visually inspect condition of coolant system hoses for cracks and deterioration | Tickalara Atlas Copco Air Compressor XAS 36YD 40 Weekly Mechanical Service | 2246636.docx | 2246636 | 001
Compressor-Air Atlas Copco XAS 36YD-TICK_A23 | Tickalara Satellite - Instrument Air - Air Compressor Package - 3800-KX-002 | Tickalara Satellite - Instrument Air - Air Compressor Package - 3800-KX-002 | 3800 - Tickalara Satellite | KICK INST AIR 3800-KX-002 | KICK | INST AIR | 3800-KX-002 | 40 | W | 04 | 00 | KICK INST AIR 40W-04-00 | KICK INST AIR 40W-04-00-001 | Change engine coolant, premix to ratio 40:1 coolant concentrate to water | Tickalara Atlas Copco Air Compressor XAS 36YD 40 Weekly Mechanical Service | 2246636.docx | 2246636 | 001
Compressor-Air Atlas Copco XAS 36YD-TICK_A23 | Tickalara Satellite - Instrument Air - Air Compressor Package - 3800-KX-002 | Tickalara Satellite - Instrument Air - Air Compressor Package - 3800-KX-002 | 3800 - Tickalara Satellite | KICK INST AIR 3800-KX-002 | KICK | INST AIR | 3800-KX-002 | 40 | W | 04 | 00 | KICK INST AIR 40W-04-00 | KICK INST AIR 40W-04-00-001 | Replace fan belt set and correct tension using belt tension tool set | Tickalara Atlas Copco Air Compressor XAS 36YD 40 Weekly Mechanical Service | 2246636.docx | 2246636 | 001
Compressor-Air Atlas Copco XAS 36YD-TICK_A23 | Tickalara Satellite - Instrument Air - Air Compressor Package - 3800-KX-002 | Tickalara Satellite - Instrument Air - Air Compressor Package - 3800-KX-002 | 3800 - Tickalara Satellite | KICK INST AIR 3800-KX-002 | KICK | INST AIR | 3800-KX-002 | 10 | W | 04 | 00 | KICK INST AIR 10W-04-00 | KICK INST AIR 10W-04-00-001 | Visually inspect exhaust emission for excessive exhaust smoke | Tickalara Atlas Copco Air Compressor XAS 36YD 10 Weekly Mechanical Service | 2245887.docx | 2245887 | 001
Compressor-Air Atlas Copco XAS 36YD-TICK_A23 | Tickalara Satellite - Instrument Air - Air Compressor Package - 3800-KX-002 | Tickalara Satellite - Instrument Air - Air Compressor Package - 3800-KX-002 | 3800 - Tickalara Satellite | KICK INST AIR 3800-KX-002 | KICK | INST AIR | 3800-KX-002 | 10 | W | 04 | 00 | KICK INST AIR 10W-04-00 | KICK INST AIR 10W-04-00-001 | Clean contact surfaces of battery terminal clamps | Tickalara Atlas Copco Air Compressor XAS 36YD 10 Weekly Mechanical Service | 2245887.docx | 2245887 | 001
Compressor-Air Atlas Copco XAS 36YD-TICK_A23 | Tickalara Satellite - Instrument Air - Air Compressor Package - 3800-KX-002 | Tickalara Satellite - Instrument Air - Air Compressor Package - 3800-KX-002 | 3800 - Tickalara Satellite | KICK INST AIR 3800-KX-002 | KICK | INST AIR | 3800-KX-002 | 40 | W | 04 | 00 | KICK INST AIR 40W-04-00 | KICK INST AIR 40W-04-00-001 | Check tightness of all compressor foundation bolts | Tickalara Atlas Copco Air Compressor XAS 36YD 40 Weekly Mechanical Service | 2246636.docx | 2246636 | 001
Compressor-Air Atlas Copco XAS 36YD-TICK_A23 | Tickalara Satellite - Instrument Air - Air Compressor Package - 3800-KX-002 | Tickalara Satellite - Instrument Air - Air Compressor Package - 3800-KX-002 | 3800 - Tickalara Satellite | KICK INST AIR 3800-KX-002 | KICK | INST AIR | 3800-KX-002 | 40 | W | 04 | 00 | KICK INST AIR 40W-04-00 | KICK INST AIR 40W-04-00-001 | Inspect purge line copper tube is not damaged or bent, fit new element for filter canister | Tickalara Atlas Copco Air Compressor XAS 36YD 40 Weekly Mechanical Service | 2246636.docx | 2246636 | 001
Compressor-Air Atlas Copco XAS 36YD-TICK_A23 | Tickalara Satellite - Instrument Air - Air Compressor Package - 3800-KX-002 | Tickalara Satellite - Instrument Air - Air Compressor Package - 3800-KX-002 | 3800 - Tickalara Satellite | KICK INST AIR 3800-KX-002 | KICK | INST AIR | 3800-KX-002 | 60 | W | 01 | 00 | KICK INST AIR 60W-01-00 | KICK INST AIR 60W-01-00-001 | Visual inspect all 3 phase and control cables for deterioration, overheating and support | Tickalara Atlas Copco Air Compressor XAS 36YD Inst/Elec Service | 2257107.docx | 2257107 | 001
Alternator Deutz F4L912-TICK_A03 | Tickalara Satellite - Power Generation - LV Alternator Package - 3800-GX-002 | Tickalara Satellite - Power Generation - LV Alternator Package - 3800-GX-002 | 3800 - Tickalara Satellite | KICK PWR GEN 3800-GX-002 | KICK | PWR GEN | 3800-GX-002 | 12 | M | 01 | 00 | KICK PWR GEN 12M-01-00 | KICK PWR GEN 12M-01-00-001 | Ensure the unit control panel indicating light are operational. Visually inspect condition of all unit contol panel buttons and meters for damage | Tickalara A/B Deutz F4L912 Alternator Inst/Elect Service | 2649151.docx | 2649151 | 001
Alternator Deutz F4L912-TICK_A03 | Tickalara Satellite - Power Generation - LV Alternator Package - 3800-GX-002 | Tickalara Satellite - Power Generation - LV Alternator Package - 3800-GX-002 | 3800 - Tickalara Satellite | KICK PWR GEN 3800-GX-002 | KICK | PWR GEN | 3800-GX-002 | 12 | M | 01 | 00 | KICK PWR GEN 12M-01-00 | KICK PWR GEN 12M-01-00-001 | Perform insulation test on main alternator windings on main alternator windings | Tickalara A/B Deutz F4L912 Alternator Inst/Elect Service | 2649151.docx | 2649151 | 001
Alternator Deutz F4L912-TICK_A03 | Tickalara Satellite - Power Generation - LV Alternator Package - 3800-GX-002 | Tickalara Satellite - Power Generation - LV Alternator Package - 3800-GX-002 | 3800 - Tickalara Satellite | KICK PWR GEN 3800-GX-002 | KICK | PWR GEN | 3800-GX-002 | 12 | M | 01 | 00 | KICK PWR GEN 12M-01-00 | KICK PWR GEN 12M-01-00-001 | Visually inspect main power cable from alternator to the circuit breaker for abrasion, cuts or scoring, loose or missing supports. Perform insulation test | Tickalara A/B Deutz F4L912 Alternator Inst/Elect Service | 2649151.docx | 2649151 | 001
Alternator Deutz F4L912-TICK_A03 | Tickalara Satellite - Power Generation - LV Alternator Package - 3800-GX-002 | Tickalara Satellite - Power Generation - LV Alternator Package - 3800-GX-002 | 3800 - Tickalara Satellite | KICK PWR GEN 3800-GX-002 | KICK | PWR GEN | 3800-GX-002 | 12 | M | 01 | 00 | KICK PWR GEN 12M-01-00 | KICK PWR GEN 12M-01-00-001 | Visually inspect alternator voltage regulator (On skid) terminals and circuit wiring connections and exterior condition | Tickalara A/B Deutz F4L912 Alternator Inst/Elect Service | 2649151.docx | 2649151 | 001
Alternator Deutz F4L912-TICK_A03 | Tickalara Satellite - Power Generation - LV Alternator Package - 3800-GX-002 | Tickalara Satellite - Power Generation - LV Alternator Package - 3800-GX-002 | 3800 - Tickalara Satellite | KICK PWR GEN 3800-GX-002 | KICK | PWR GEN | 3800-GX-002 | 12 | M | 01 | 00 | KICK PWR GEN 12M-01-00 | KICK PWR GEN 12M-01-00-001 | Visually inspect alternator unit control panel (On skid) all other terminals and circuit wiring connections and clean UCP cabinet | Tickalara A/B Deutz F4L912 Alternator Inst/Elect Service | 2649151.docx | 2649151 | 001
Alternator Deutz F4L912-TICK_A03 | Tickalara Satellite - Power Generation - LV Alternator Package - 3800-GX-002 | Tickalara Satellite - Power Generation - LV Alternator Package - 3800-GX-002 | 3800 - Tickalara Satellite | KICK PWR GEN 3800-GX-002 | KICK | PWR GEN | 3800-GX-002 | 12 | M | 01 | 00 | KICK PWR GEN 12M-01-00 | KICK PWR GEN 12M-01-00-001 | Visually inspect alternator main terminal box (External) for of corossion and check earth cable connection for tightness | Tickalara A/B Deutz F4L912 Alternator Inst/Elect Service | 2649151.docx | 2649151 | 001
Alternator Deutz F4L912-TICK_A03 | Tickalara Satellite - Power Generation - LV Alternator Package - 3800-GX-002 | Tickalara Satellite - Power Generation - LV Alternator Package - 3800-GX-002 | 3800 - Tickalara Satellite | KICK PWR GEN 3800-GX-002 | KICK | PWR GEN | 3800-GX-002 | 12 | M | 01 | 00 | KICK PWR GEN 12M-01-00 | KICK PWR GEN 12M-01-00-001 | Visually inspect alternator load sensor/governor (On skid) circuit wiring connections and all load sensing CT's for sign of heat discolouration. | Tickalara A/B Deutz F4L912 Alternator Inst/Elect Service | 2649151.docx | 2649151 | 001
Alternator Deutz F4L912-TICK_A03 | Tickalara Satellite - Power Generation - LV Alternator Package - 3800-GX-002 | Tickalara Satellite - Power Generation - LV Alternator Package - 3800-GX-002 | 3800 - Tickalara Satellite | KICK PWR GEN 3800-GX-002 | KICK | PWR GEN | 3800-GX-002 | 12 | M | 01 | 00 | KICK PWR GEN 12M-01-00 | KICK PWR GEN 12M-01-00-001 | Measure the alternator bearings vibration and analyse the bearing condition | Tickalara A/B Deutz F4L912 Alternator Inst/Elect Service | 2649151.docx | 2649151 | 001
Alternator Deutz F4L912-TICK_A03 | Tickalara Satellite - Power Generation - LV Alternator Package - 3800-GX-002 | Tickalara Satellite - Power Generation - LV Alternator Package - 3800-GX-002 | 3800 - Tickalara Satellite | KICK PWR GEN 3800-GX-002 | KICK | PWR GEN | 3800-GX-002 | 12 | M | 01 | 00 | KICK PWR GEN 12M-01-00 | KICK PWR GEN 12M-01-00-001 | Check alternator batteries electrolyte level and inspect battery terminals for corossion, clean as required | Tickalara A/B Deutz F4L912 Alternator Inst/Elect Service | 2649151.docx | 2649151 | 001
Alternator Deutz F4L912-TICK_A03 | Tickalara Satellite - Power Generation - LV Alternator Package - 3800-GX-002 | Tickalara Satellite - Power Generation - LV Alternator Package - 3800-GX-002 | 3800 - Tickalara Satellite | KICK PWR GEN 3800-GX-002 | KICK | PWR GEN | 3800-GX-002 | 12 | M | 01 | 00 | KICK PWR GEN 12M-01-00 | KICK PWR GEN 12M-01-00-001 | Check alternator battery charger amp meter, float voltage and boost voltage, inspect the condition of all charger panel meters | Tickalara A/B Deutz F4L912 Alternator Inst/Elect Service | 2649151.docx | 2649151 | 001
Alternator Deutz F4L912-TICK_A03 | Tickalara Satellite - Power Generation - LV Alternator Package - 3800-GX-002 | Tickalara Satellite - Power Generation - LV Alternator Package - 3800-GX-002 | 3800 - Tickalara Satellite | KICK PWR GEN 3800-GX-002 | KICK | PWR GEN | 3800-GX-002 | 12 | M | 01 | 00 | KICK PWR GEN 12M-01-00 | KICK PWR GEN 12M-01-00-001 | Visually inspect exterior of alternator unit for damage, missing bolts, missing or loose covers, missing cable ties, or a build up of oil or dust | Tickalara A/B Deutz F4L912 Alternator Inst/Elect Service | 2649151.docx | 2649151 | 001
Alternator Deutz F4L912-TICK_A03 | Tickalara Satellite - Power Generation - LV Alternator Package - 3800-GX-002 | Tickalara Satellite - Power Generation - LV Alternator Package - 3800-GX-002 | 3800 - Tickalara Satellite | KICK PWR GEN 3800-GX-002 | KICK | PWR GEN | 3800-GX-002 | 12 | M | 01 | 00 | KICK PWR GEN 12M-01-00 | KICK PWR GEN 12M-01-00-001 | Test run alternator and perform load test, visually inspect the condition of all meters (On skid and switchroom) and ensure they operate as expected | Tickalara A/B Deutz F4L912 Alternator Inst/Elect Service | 2649151.docx | 2649151 | 001
Alternator Deutz F4L912-TICK_A03 | Tickalara Satellite - Power Generation - LV Alternator Package - 3800-GX-002 | Tickalara Satellite - Power Generation - LV Alternator Package - 3800-GX-002 | 3800 - Tickalara Satellite | KICK PWR GEN 3800-GX-002 | KICK | PWR GEN | 3800-GX-002 | 12 | M | 01 | 00 | KICK PWR GEN 12M-01-00 | KICK PWR GEN 12M-01-00-001 | Check the alternator main circuit breaker fixing bolts for tightness | Tickalara A/B Deutz F4L912 Alternator Inst/Elect Service | 2649151.docx | 2649151 | 001
Alternator Deutz F4L912-TICK_A03 | Tickalara Satellite - Power Generation - LV Alternator Package - 3800-GX-002 | Tickalara Satellite - Power Generation - LV Alternator Package - 3800-GX-002 | 3800 - Tickalara Satellite | KICK PWR GEN 3800-GX-002 | KICK | PWR GEN | 3800-GX-002 | 12 | M | 01 | 00 | KICK PWR GEN 12M-01-00 | KICK PWR GEN 12M-01-00-001 | Test residual current device (RCD) trip button | Tickalara A/B Deutz F4L912 Alternator Inst/Elect Service | 2649151.docx | 2649151 | 001
Alternator Deutz F4L912-TICK_A03 | Tickalara Satellite - Power Generation - LV Alternator Package - 3800-GX-003 | Tickalara Satellite - Power Generation - LV Alternator Package - 3800-GX-003 | 3800 - Tickalara Satellite | KICK PWR GEN 3800-GX-003 | KICK | PWR GEN | 3800-GX-003 | 12 | M | 01 | 00 | KICK PWR GEN 12M-01-00 | KICK PWR GEN 12M-01-00-001 | Ensure the unit control panel indicating light are operational. Visually inspect condition of all unit contol panel buttons and meters for damage | Tickalara A/B Deutz F4L912 Alternator Inst/Elect Service | 2649151.docx | 2649151 | 001
Alternator Deutz F4L912-TICK_A03 | Tickalara Satellite - Power Generation - LV Alternator Package - 3800-GX-003 | Tickalara Satellite - Power Generation - LV Alternator Package - 3800-GX-003 | 3800 - Tickalara Satellite | KICK PWR GEN 3800-GX-003 | KICK | PWR GEN | 3800-GX-003 | 12 | M | 01 | 00 | KICK PWR GEN 12M-01-00 | KICK PWR GEN 12M-01-00-001 | Perform insulation test on main alternator windings on main alternator windings | Tickalara A/B Deutz F4L912 Alternator Inst/Elect Service | 2649151.docx | 2649151 | 001
Alternator Deutz F4L912-TICK_A03 | Tickalara Satellite - Power Generation - LV Alternator Package - 3800-GX-003 | Tickalara Satellite - Power Generation - LV Alternator Package - 3800-GX-003 | 3800 - Tickalara Satellite | KICK PWR GEN 3800-GX-003 | KICK | PWR GEN | 3800-GX-003 | 12 | M | 01 | 00 | KICK PWR GEN 12M-01-00 | KICK PWR GEN 12M-01-00-001 | Measure the alternator bearings vibration and analyse the bearing condition | Tickalara A/B Deutz F4L912 Alternator Inst/Elect Service | 2649151.docx | 2649151 | 001
Alternator Deutz F4L912-TICK_A03 | Tickalara Satellite - Power Generation - LV Alternator Package - 3800-GX-003 | Tickalara Satellite - Power Generation - LV Alternator Package - 3800-GX-003 | 3800 - Tickalara Satellite | KICK PWR GEN 3800-GX-003 | KICK | PWR GEN | 3800-GX-003 | 12 | M | 01 | 00 | KICK PWR GEN 12M-01-00 | KICK PWR GEN 12M-01-00-001 | Test run alternator and perform load test, visually inspect the condition of all meters (On skid and switchroom) and ensure they operate as expected | Tickalara A/B Deutz F4L912 Alternator Inst/Elect Service | 2649151.docx | 2649151 | 001
Alternator Deutz F4L912-TICK_A03 | Tickalara Satellite - Power Generation - LV Alternator Package - 3800-GX-003 | Tickalara Satellite - Power Generation - LV Alternator Package - 3800-GX-003 | 3800 - Tickalara Satellite | KICK PWR GEN 3800-GX-003 | KICK | PWR GEN | 3800-GX-003 | 12 | M | 01 | 00 | KICK PWR GEN 12M-01-00 | KICK PWR GEN 12M-01-00-001 | Visually inspect exterior of alternator unit for damage, missing bolts, missing or loose covers, missing cable ties, or a build up of oil or dust | Tickalara A/B Deutz F4L912 Alternator Inst/Elect Service | 2649151.docx | 2649151 | 001
Alternator Deutz F4L912-TICK_A03 | Tickalara Satellite - Power Generation - LV Alternator Package - 3800-GX-003 | Tickalara Satellite - Power Generation - LV Alternator Package - 3800-GX-003 | 3800 - Tickalara Satellite | KICK PWR GEN 3800-GX-003 | KICK | PWR GEN | 3800-GX-003 | 12 | M | 01 | 00 | KICK PWR GEN 12M-01-00 | KICK PWR GEN 12M-01-00-001 | Check alternator battery charger amp meter, float voltage and boost voltage, inspect the condition of all charger panel meters | Tickalara A/B Deutz F4L912 Alternator Inst/Elect Service | 2649151.docx | 2649151 | 001
Alternator Deutz F4L912-TICK_A03 | Tickalara Satellite - Power Generation - LV Alternator Package - 3800-GX-003 | Tickalara Satellite - Power Generation - LV Alternator Package - 3800-GX-003 | 3800 - Tickalara Satellite | KICK PWR GEN 3800-GX-003 | KICK | PWR GEN | 3800-GX-003 | 12 | M | 01 | 00 | KICK PWR GEN 12M-01-00 | KICK PWR GEN 12M-01-00-001 | Check alternator batteries electrolyte level and inspect battery terminals for corossion, clean as required | Tickalara A/B Deutz F4L912 Alternator Inst/Elect Service | 2649151.docx | 2649151 | 001
Alternator Deutz F4L912-TICK_A03 | Tickalara Satellite - Power Generation - LV Alternator Package - 3800-GX-003 | Tickalara Satellite - Power Generation - LV Alternator Package - 3800-GX-003 | 3800 - Tickalara Satellite | KICK PWR GEN 3800-GX-003 | KICK | PWR GEN | 3800-GX-003 | 12 | M | 01 | 00 | KICK PWR GEN 12M-01-00 | KICK PWR GEN 12M-01-00-001 | Visually inspect alternator load sensor/governor (On skid) circuit wiring connections and all load sensing CT's for sign of heat discolouration. | Tickalara A/B Deutz F4L912 Alternator Inst/Elect Service | 2649151.docx | 2649151 | 001
Alternator Deutz F4L912-TICK_A03 | Tickalara Satellite - Power Generation - LV Alternator Package - 3800-GX-003 | Tickalara Satellite - Power Generation - LV Alternator Package - 3800-GX-003 | 3800 - Tickalara Satellite | KICK PWR GEN 3800-GX-003 | KICK | PWR GEN | 3800-GX-003 | 12 | M | 01 | 00 | KICK PWR GEN 12M-01-00 | KICK PWR GEN 12M-01-00-001 | Visually inspect alternator main terminal box (External) for of corossion and check earth cable connection for tightness | Tickalara A/B Deutz F4L912 Alternator Inst/Elect Service | 2649151.docx | 2649151 | 001
Alternator Deutz F4L912-TICK_A03 | Tickalara Satellite - Power Generation - LV Alternator Package - 3800-GX-003 | Tickalara Satellite - Power Generation - LV Alternator Package - 3800-GX-003 | 3800 - Tickalara Satellite | KICK PWR GEN 3800-GX-003 | KICK | PWR GEN | 3800-GX-003 | 12 | M | 01 | 00 | KICK PWR GEN 12M-01-00 | KICK PWR GEN 12M-01-00-001 | Visually inspect alternator unit control panel (On skid) all other terminals and circuit wiring connections and clean UCP cabinet | Tickalara A/B Deutz F4L912 Alternator Inst/Elect Service | 2649151.docx | 2649151 | 001
Alternator Deutz F4L912-TICK_A03 | Tickalara Satellite - Power Generation - LV Alternator Package - 3800-GX-003 | Tickalara Satellite - Power Generation - LV Alternator Package - 3800-GX-003 | 3800 - Tickalara Satellite | KICK PWR GEN 3800-GX-003 | KICK | PWR GEN | 3800-GX-003 | 12 | M | 01 | 00 | KICK PWR GEN 12M-01-00 | KICK PWR GEN 12M-01-00-001 | Visually inspect main power cable from alternator to the circuit breaker for abrasion, cuts or scoring, loose or missing supports. Perform insulation test | Tickalara A/B Deutz F4L912 Alternator Inst/Elect Service | 2649151.docx | 2649151 | 001
Alternator Deutz F4L912-TICK_A03 | Tickalara Satellite - Power Generation - LV Alternator Package - 3800-GX-003 | Tickalara Satellite - Power Generation - LV Alternator Package - 3800-GX-003 | 3800 - Tickalara Satellite | KICK PWR GEN 3800-GX-003 | KICK | PWR GEN | 3800-GX-003 | 12 | M | 01 | 00 | KICK PWR GEN 12M-01-00 | KICK PWR GEN 12M-01-00-001 | Visually inspect alternator voltage regulator (On skid) terminals and circuit wiring connections and exterior condition | Tickalara A/B Deutz F4L912 Alternator Inst/Elect Service | 2649151.docx | 2649151 | 001
Alternator Deutz F4L912-TICK_A03 | Tickalara Satellite - Power Generation - LV Alternator Package - 3800-GX-003 | Tickalara Satellite - Power Generation - LV Alternator Package - 3800-GX-003 | 3800 - Tickalara Satellite | KICK PWR GEN 3800-GX-003 | KICK | PWR GEN | 3800-GX-003 | 12 | M | 01 | 00 | KICK PWR GEN 12M-01-00 | KICK PWR GEN 12M-01-00-001 | Check the alternator main circuit breaker fixing bolts for tightness | Tickalara A/B Deutz F4L912 Alternator Inst/Elect Service | 2649151.docx | 2649151 | 001
Alternator Deutz F4L912-TICK_A03 | Tickalara Satellite - Power Generation - LV Alternator Package - 3800-GX-003 | Tickalara Satellite - Power Generation - LV Alternator Package - 3800-GX-003 | 3800 - Tickalara Satellite | KICK PWR GEN 3800-GX-003 | KICK | PWR GEN | 3800-GX-003 | 12 | M | 01 | 00 | KICK PWR GEN 12M-01-00 | KICK PWR GEN 12M-01-00-001 | Test residual current device (RCD) trip button | Tickalara A/B Deutz F4L912 Alternator Inst/Elect Service | 2649151.docx | 2649151 | 001
Managed by Parent Maintenance_A02 | Tickalara Satellite - Buildings - Office | Tickalara Satellite - Buildings - Office | 3800 - Tickalara Satellite | KICK BLD 3800-DB-001 |  |  | 3800-DB-001 | [5 empty] | Managed by Parent Maintenance | Managed by Parent Maintenance | Managed by Parent Maintenance | Managed by Parent Maintenance | Managed by Parent Maintenance
Managed by Parent Maintenance_A02 | Tickalara Satellite - Buildings - Office | Tickalara Satellite - Buildings - Office | 3800 - Tickalara Satellite | KICK BLD 3800-BLD-001-BUFI-2 |  |  | 3800-BLD-001-BUFI-2 | [5 empty] | Managed by Parent Maintenance | Managed by Parent Maintenance | Managed by Parent Maintenance | Managed by Parent Maintenance | Managed by Parent Maintenance
Managed by Parent Maintenance_A02 | Tickalara Satellite - Buildings - Office | Tickalara Satellite - Buildings - Office | 3800 - Tickalara Satellite | KICK BLD 3800-DB-N6 |  |  | 3800-DB-N6 | [5 empty] | Managed by Parent Maintenance | Managed by Parent Maintenance | Managed by Parent Maintenance | Managed by Parent Maintenance | Managed by Parent Maintenance
Managed by Parent Maintenance_A02 | Tickalara Satellite - Buildings - Workshop | Tickalara Satellite - Buildings - Workshop | 3800 - Tickalara Satellite | KICK BLD 3800-BLD-002 |  |  | 3800-BLD-002 | [5 empty] | Managed by Parent Maintenance | Managed by Parent Maintenance | Managed by Parent Maintenance | Managed by Parent Maintenance | Managed by Parent Maintenance
Managed by Parent Maintenance_A02 | Tickalara Satellite - Buildings - Office | Tickalara Satellite - Buildings - Office | 3800 - Tickalara Satellite | KICK BLD 3800-DB-006 |  |  | 3800-DB-006 | [5 empty] | Managed by Parent Maintenance | Managed by Parent Maintenance | Managed by Parent Maintenance | Managed by Parent Maintenance | Managed by Parent Maintenance
Managed by Parent Maintenance_A02 | Tickalara Satellite - Buildings - Office | Tickalara Satellite - Buildings - Office | 3800 - Tickalara Satellite | KICK BLD 3800-DB-005 |  |  | 3800-DB-005 | [5 empty] | Managed by Parent Maintenance | Managed by Parent Maintenance | Managed by Parent Maintenance | Managed by Parent Maintenance | Managed by Parent Maintenance
Managed by Parent Maintenance_A02 | Tickalara Satellite - Buildings - Workshop | Tickalara Satellite - Buildings - Workshop | 3800 - Tickalara Satellite | KICK BLD 3800-DB-003 |  |  | 3800-DB-003 | [5 empty] | Managed by Parent Maintenance | Managed by Parent Maintenance | Managed by Parent Maintenance | Managed by Parent Maintenance | Managed by Parent Maintenance
Managed by Parent Maintenance_A02 | Tickalara Satellite - Buildings - Workshop | Tickalara Satellite - Buildings - Workshop | 3800 - Tickalara Satellite | KICK BLD 3800-BLD-004 |  |  | 3800-BLD-004 | [5 empty] | Managed by Parent Maintenance | Managed by Parent Maintenance | Managed by Parent Maintenance | Managed by Parent Maintenance | Managed by Parent Maintenance
Managed by Parent Maintenance_A02 | Tickalara Satellite - Buildings - Workshop | Tickalara Satellite - Buildings - Workshop | 3800 - Tickalara Satellite | KICK BLD 3800-DB-002 |  |  | 3800-DB-002 | [5 empty] | Managed by Parent Maintenance | Managed by Parent Maintenance | Managed by Parent Maintenance | Managed by Parent Maintenance | Managed by Parent Maintenance
Managed by Parent Maintenance_A02 | Tickalara Satellite - Buildings - Office | Tickalara Satellite - Buildings - Office | 3800 - Tickalara Satellite | KICK BLD 3800-DB-N4 |  |  | 3800-DB-N4 | [5 empty] | Managed by Parent Maintenance | Managed by Parent Maintenance | Managed by Parent Maintenance | Managed by Parent Maintenance | Managed by Parent Maintenance
Managed by Parent Maintenance_A02 | Tickalara Satellite - Buildings - Office | Tickalara Satellite - Buildings - Office | 3800 - Tickalara Satellite | KICK BLD 3800-BLD-001-INS |  |  | 3800-BLD-001-INS | [5 empty] | Managed by Parent Maintenance | Managed by Parent Maintenance | Managed by Parent Maintenance | Managed by Parent Maintenance | Managed by Parent Maintenance
Managed by Parent Maintenance_A02 | Tickalara Satellite - Buildings - Office | Tickalara Satellite - Buildings - Office | 3800 - Tickalara Satellite | KICK BLD 3800-BLD-001-BUFI-1 |  |  | 3800-BLD-001-BUFI-1 | [5 empty] | Managed by Parent Maintenance | Managed by Parent Maintenance | Managed by Parent Maintenance | Managed by Parent Maintenance | Managed by Parent Maintenance
Managed by Parent Maintenance_A02 | Tickalara Satellite - Buildings - Workshop | Tickalara Satellite - Buildings - Workshop | 3800 - Tickalara Satellite | KICK BLD 3800-BLD-003 |  |  | 3800-BLD-003 | [5 empty] | Managed by Parent Maintenance | Managed by Parent Maintenance | Managed by Parent Maintenance | Managed by Parent Maintenance | Managed by Parent Maintenance
Managed by Parent Maintenance_A02 | Tickalara Satellite - Buildings - Office | Tickalara Satellite - Buildings - Office | 3800 - Tickalara Satellite | KICK BLD 3800-DB-N8 |  |  | 3800-DB-N8 | [5 empty] | Managed by Parent Maintenance | Managed by Parent Maintenance | Managed by Parent Maintenance | Managed by Parent Maintenance | Managed by Parent Maintenance
Managed by Parent Maintenance_A02 | Tickalara Satellite - Buildings - Office | Tickalara Satellite - Buildings - Office | 3800 - Tickalara Satellite | KICK BLD 3800-DB-N10 |  |  | 3800-DB-N10 | [5 empty] | Managed by Parent Maintenance | Managed by Parent Maintenance | Managed by Parent Maintenance | Managed by Parent Maintenance | Managed by Parent Maintenance
Managed by Parent Maintenance_A02 | Tickalara Satellite - Buildings - Office | Tickalara Satellite - Buildings - Office | 3800 - Tickalara Satellite | KICK BLD 3800-BLD-001 |  |  | 3800-BLD-001 | [5 empty] | Managed by Parent Maintenance | Managed by Parent Maintenance | Managed by Parent Maintenance | Managed by Parent Maintenance | Managed by Parent Maintenance
Managed by Parent Maintenance_A02 | Tickalara Satellite - Buildings - Office | Tickalara Satellite - Buildings - Office | 3800 - Tickalara Satellite | KICK BLD 3800-DB-007 |  |  | 3800-DB-007 | [5 empty] | Managed by Parent Maintenance | Managed by Parent Maintenance | Managed by Parent Maintenance | Managed by Parent Maintenance | Managed by Parent Maintenance
Managed by Parent Maintenance_A02 | Tickalara Satellite - Crude Oil Storage - Production Tanks | Tickalara Satellite - Crude Oil Storage - Production Tanks | 3800 - Tickalara Satellite | KICK CRUDE OIL STRG 3800-LIT-0344 |  |  | 3800-LIT-0344 | [5 empty] | Managed by Parent Maintenance | Managed by Parent Maintenance | Managed by Parent Maintenance | Managed by Parent Maintenance | Managed by Parent Maintenance
Managed by Parent Maintenance_A02 | Tickalara Satellite - Crude Oil Storage - Production Tanks | Tickalara Satellite - Crude Oil Storage - Production Tanks | 3800 - Tickalara Satellite | KICK CRUDE OIL STRG 3800-LSH-0087 |  |  | 3800-LSH-0087 | [5 empty] | Managed by Parent Maintenance | Managed by Parent Maintenance | Managed by Parent Maintenance | Managed by Parent Maintenance | Managed by Parent Maintenance
Managed by Integrity_A01 | Tickalara Satellite - Crude Oil Storage - Production Tanks | Tickalara Satellite - Crude Oil Storage - Production Tanks | 3800 - Tickalara Satellite | KICK CRUDE OIL STRG 3800-LSHH-0053 |  |  | 3800-LSHH-0053 | [5 empty] | Managed by Integrity | Managed by Integrity | Managed by Integrity | Managed by Integrity | Managed by Integrity
Parent Asset - Maintenance covered by children_A03 | Tickalara Satellite - Crude Oil Storage - Dewatering / Test Tanks | Tickalara Satellite - Crude Oil Storage - Dewatering / Test Tanks | 3800 - Tickalara Satellite | KICK CRUDE OIL STRG 3800-SAT-STO-DEW |  |  | 3800-SAT-STO-DEW | [5 empty] | Maintenance covered by children | Maintenance covered by children | Parent Asset | Parent Asset | Parent Asset
Managed by Integrity_A01 | Tickalara Satellite - Crude Oil Storage - Production Tanks | Tickalara Satellite - Crude Oil Storage - Production Tanks | 3800 - Tickalara Satellite | KICK CRUDE OIL STRG 3800-TK-003C |  |  | 3800-TK-003C | [5 empty] | Managed by Integrity | Managed by Integrity | Managed by Integrity | Managed by Integrity | Managed by Integrity
Managed by Integrity_A01 | Tickalara Satellite - Crude Oil Storage - Production Tanks | Tickalara Satellite - Crude Oil Storage - Production Tanks | 3800 - Tickalara Satellite | KICK CRUDE OIL STRG 3800-LIT-0088 |  |  | 3800-LIT-0088 | [5 empty] | Managed by Integrity | Managed by Integrity | Managed by Integrity | Managed by Integrity | Managed by Integrity
Managed by Parent Maintenance_A02 | Tickalara Satellite - Crude Oil Storage - Dewatering / Test Tanks | Tickalara Satellite - Crude Oil Storage - Dewatering / Test Tanks | 3800 - Tickalara Satellite | KICK CRUDE OIL STRG 3800-PX-003 |  |  | 3800-PX-003 | [5 empty] | Managed by Parent Maintenance | Managed by Parent Maintenance | Managed by Parent Maintenance | Managed by Parent Maintenance | Managed by Parent Maintenance
Managed by Integrity_A01 | Tickalara Satellite - Crude Oil Storage - Production Tanks | Tickalara Satellite - Crude Oil Storage - Production Tanks | 3800 - Tickalara Satellite | KICK CRUDE OIL STRG 3800-LSHH-0261 |  |  | 3800-LSHH-0261 | [5 empty] | Managed by Integrity | Managed by Integrity | Managed by Integrity | Managed by Integrity | Managed by Integrity
Managed by Integrity_A01 | Tickalara Satellite - Crude Oil Storage - Production Tanks | Tickalara Satellite - Crude Oil Storage - Production Tanks | 3800 - Tickalara Satellite | KICK CRUDE OIL STRG 3800-TK-003E |  |  | 3800-TK-003E | [5 empty] | Managed by Integrity | Managed by Integrity | Managed by Integrity | Managed by Integrity | Managed by Integrity
Managed by Integrity_A01 | Tickalara Satellite - Crude Oil Storage - Dewatering / Test Tanks | Tickalara Satellite - Crude Oil Storage - Dewatering / Test Tanks | 3800 - Tickalara Satellite | KICK CRUDE OIL STRG 3800-TK-001A |  |  | 3800-TK-001A | [5 empty] | Managed by Integrity | Managed by Integrity | Managed by Integrity | Managed by Integrity | Managed by Integrity
Managed by Parent Maintenance_A02 | Tickalara Satellite - Crude Oil Storage - Production Tanks | Tickalara Satellite - Crude Oil Storage - Production Tanks | 3800 - Tickalara Satellite | KICK CRUDE OIL STRG 3800-TK-003E-CO |  |  | 3800-TK-003E-CO | [5 empty] | Managed by Parent Maintenance | Managed by Parent Maintenance | Managed by Parent Maintenance | Managed by Parent Maintenance | Managed by Parent Maintenance
Managed by Integrity_A01 | Tickalara Satellite - Crude Oil Storage - Dewatering / Test Tanks | Tickalara Satellite - Crude Oil Storage - Dewatering / Test Tanks | 3800 - Tickalara Satellite | KICK CRUDE OIL STRG 3800-LSHH-0055 |  |  | 3800-LSHH-0055 | [5 empty] | Managed by Integrity | Managed by Integrity | Managed by Integrity | Managed by Integrity | Managed by Integrity
Parent Asset - Maintenance covered by children_A03 | Tickalara Satellite - Crude Oil Storage - Dewatering / Test Tanks | Tickalara Satellite - Crude Oil Storage - Dewatering / Test Tanks | 3800 - Tickalara Satellite | KICK CRUDE OIL STRG 3800-SAT-STO-CHEM-BND |  |  | 3800-SAT-STO-CHEM-BND | [5 empty] | Maintenance covered by children | Maintenance covered by children | Parent Asset | Parent Asset | Parent Asset
Parent Asset - Maintenance covered by children_A03 | Tickalara Satellite - Crude Oil Storage - Tank Farm Bund | Tickalara Satellite - Crude Oil Storage - Tank Farm Bund | 3800 - Tickalara Satellite | KICK CRUDE OIL STRG 3800-SAT-STO-BND |  |  | 3800-SAT-STO-BND | [5 empty] | Maintenance covered by children | Maintenance covered by children | Parent Asset | Parent Asset | Parent Asset
Managed by Parent Maintenance_A02 | Tickalara Satellite - Crude Oil Storage - Production Tanks | Tickalara Satellite - Crude Oil Storage - Production Tanks | 3800 - Tickalara Satellite | KICK CRUDE OIL STRG 3800-TK-003B-CO |  |  | 3800-TK-003B-CO | [5 empty] | Managed by Parent Maintenance | Managed by Parent Maintenance | Managed by Parent Maintenance | Managed by Parent Maintenance | Managed by Parent Maintenance
Managed by Integrity_A01 | Tickalara Satellite - Crude Oil Storage - Production Tanks | Tickalara Satellite - Crude Oil Storage - Production Tanks | 3800 - Tickalara Satellite | KICK CRUDE OIL STRG 3800-TK-003D |  |  | 3800-TK-003D | [5 empty] | Managed by Integrity | Managed by Integrity | Managed by Integrity | Managed by Integrity | Managed by Integrity
Managed by Parent Maintenance_A02 | Tickalara Satellite - Crude Oil Storage - Production Tanks | Tickalara Satellite - Crude Oil Storage - Production Tanks | 3800 - Tickalara Satellite | KICK CRUDE OIL STRG 3800-TK-003A-CO |  |  | 3800-TK-003A-CO | [5 empty] | Managed by Parent Maintenance | Managed by Parent Maintenance | Managed by Parent Maintenance | Managed by Parent Maintenance | Managed by Parent Maintenance
Managed by Parent Maintenance_A02 | Tickalara Satellite - Crude Oil Storage - Production Tanks | Tickalara Satellite - Crude Oil Storage - Production Tanks | 3800 - Tickalara Satellite | KICK CRUDE OIL STRG 3800-LSHH-0345 |  |  | 3800-LSHH-0345 | [5 empty] | Managed by Parent Maintenance | Managed by Parent Maintenance | Managed by Parent Maintenance | Managed by Parent Maintenance | Managed by Parent Maintenance
Parent Asset - Maintenance covered by children_A03 | Tickalara Satellite - Crude Oil Storage - Production Tanks | Tickalara Satellite - Crude Oil Storage - Production Tanks | 3800 - Tickalara Satellite | KICK CRUDE OIL STRG 3800-SAT-STO-PRO |  |  | 3800-SAT-STO-PRO | [5 empty] | Maintenance covered by children | Maintenance covered by children | Parent Asset | Parent Asset | Parent Asset
Managed by Parent Maintenance_A02 | Tickalara Satellite - Crude Oil Storage - Production Tanks | Tickalara Satellite - Crude Oil Storage - Production Tanks | 3800 - Tickalara Satellite | KICK CRUDE OIL STRG 3800-LIC-0059 |  |  | 3800-LIC-0059 | [5 empty] | Managed by Parent Maintenance | Managed by Parent Maintenance | Managed by Parent Maintenance | Managed by Parent Maintenance | Managed by Parent Maintenance
Managed by Parent Maintenance_A02 | Tickalara Satellite - Crude Oil Storage - Production Tanks | Tickalara Satellite - Crude Oil Storage - Production Tanks | 3800 - Tickalara Satellite | KICK CRUDE OIL STRG 3800-TK-003D-CO |  |  | 3800-TK-003D-CO | [5 empty] | Managed by Parent Maintenance | Managed by Parent Maintenance | Managed by Parent Maintenance | Managed by Parent Maintenance | Managed by Parent Maintenance
Managed by Integrity_A01 | Tickalara Satellite - Crude Oil Storage - Production Tanks | Tickalara Satellite - Crude Oil Storage - Production Tanks | 3800 - Tickalara Satellite | KICK CRUDE OIL STRG 3800-TK-048 |  |  | 3800-TK-048 | [5 empty] | Managed by Integrity | Managed by Integrity | Managed by Integrity | Managed by Integrity | Managed by Integrity
Managed by Integrity_A01 | Tickalara Satellite - Crude Oil Storage - Production Tanks | Tickalara Satellite - Crude Oil Storage - Production Tanks | 3800 - Tickalara Satellite | KICK CRUDE OIL STRG 3800-TK-003A |  |  | 3800-TK-003A | [5 empty] | Managed by Integrity | Managed by Integrity | Managed by Integrity | Managed by Integrity | Managed by Integrity
Managed by Integrity_A01 | Tickalara Satellite - Crude Oil Storage - Production Tanks | Tickalara Satellite - Crude Oil Storage - Production Tanks | 3800 - Tickalara Satellite | KICK CRUDE OIL STRG 3800-TK-003B |  |  | 3800-TK-003B | [5 empty] | Managed by Integrity | Managed by Integrity | Managed by Integrity | Managed by Integrity | Managed by Integrity
Managed by Integrity_A01 | Tickalara Satellite - Crude Oil Storage - Production Tanks | Tickalara Satellite - Crude Oil Storage - Production Tanks | 3800 - Tickalara Satellite | KICK CRUDE OIL STRG 3800-LSLL-0004 |  |  | 3800-LSLL-0004 | [5 empty] | Managed by Integrity | Managed by Integrity | Managed by Integrity | Managed by Integrity | Managed by Integrity
Managed by Parent Maintenance_A02 | Tickalara Satellite - Export - Control and Monitor | Tickalara Satellite - Export - Control and Monitor | 3800 - Tickalara Satellite | KICK EXP 3800-FIT-0129 |  |  | 3800-FIT-0129 | [5 empty] | Managed by Parent Maintenance | Managed by Parent Maintenance | Managed by Parent Maintenance | Managed by Parent Maintenance | Managed by Parent Maintenance
Managed by Integrity_A01 | Tickalara Satellite - Export - Shipping Pumps | Tickalara Satellite - Export - Shipping Pumps | 3800 - Tickalara Satellite | KICK EXP 3800-V-001B |  |  | 3800-V-001B | [5 empty] | Managed by Integrity | Managed by Integrity | Managed by Integrity | Managed by Integrity | Managed by Integrity
Managed by Parent Maintenance_A02 | Tickalara Satellite - Export - Control and Monitor | Tickalara Satellite - Export - Control and Monitor | 3800 - Tickalara Satellite | KICK EXP 3800-FE-0128 |  |  | 3800-FE-0128 | [5 empty] | Managed by Parent Maintenance | Managed by Parent Maintenance | Managed by Parent Maintenance | Managed by Parent Maintenance | Managed by Parent Maintenance
Parent Asset - Maintenance covered by children_A03 | Tickalara Satellite - Export - Shipping Pumps | Tickalara Satellite - Export - Shipping Pumps | 3800 - Tickalara Satellite | KICK EXP 3800-PX-001A |  |  | 3800-PX-001A | [5 empty] | Maintenance covered by children | Maintenance covered by children | Parent Asset | Parent Asset | Parent Asset
Managed by Integrity_A01 | Tickalara Satellite - Export - Shipping Pumps | Tickalara Satellite - Export - Shipping Pumps | 3800 - Tickalara Satellite | KICK EXP 3800-V-020 |  |  | 3800-V-020 | [5 empty] | Managed by Integrity | Managed by Integrity | Managed by Integrity | Managed by Integrity | Managed by Integrity
Managed by Integrity_A01 | Tickalara Satellite - Export - Shipping Pumps | Tickalara Satellite - Export - Shipping Pumps | 3800 - Tickalara Satellite | KICK EXP 3800-V-019 |  |  | 3800-V-019 | [5 empty] | Managed by Integrity | Managed by Integrity | Managed by Integrity | Managed by Integrity | Managed by Integrity
Parent Asset - Maintenance covered by children_A03 | Tickalara Satellite - Export - Shipping Pumps | Tickalara Satellite - Export - Shipping Pumps | 3800 - Tickalara Satellite | KICK EXP 3800-SAT-EXP-PUM-BND |  |  | 3800-SAT-EXP-PUM-BND | [5 empty] | Maintenance covered by children | Maintenance covered by children | Parent Asset | Parent Asset | Parent Asset
Parent Asset - Maintenance covered by children_A03 | Tickalara Satellite - Export - Shipping Pumps | Tickalara Satellite - Export - Shipping Pumps | 3800 - Tickalara Satellite | KICK EXP 3800-PX-001B |  |  | 3800-PX-001B | [5 empty] | Maintenance covered by children | Maintenance covered by children | Parent Asset | Parent Asset | Parent Asset
Managed by Integrity_A01 | Tickalara Satellite - Export - Shipping Pumps | Tickalara Satellite - Export - Shipping Pumps | 3800 - Tickalara Satellite | KICK EXP 3800-PSLL-0004 |  |  | 3800-PSLL-0004 | [5 empty] | Managed by Integrity | Managed by Integrity | Managed by Integrity | Managed by Integrity | Managed by Integrity
Managed by Integrity_A01 | Tickalara Satellite - Export - Shipping Pumps | Tickalara Satellite - Export - Shipping Pumps | 3800 - Tickalara Satellite | KICK EXP 3800-V-018 |  |  | 3800-V-018 | [5 empty] | Managed by Integrity | Managed by Integrity | Managed by Integrity | Managed by Integrity | Managed by Integrity
Managed by Integrity_A01 | Tickalara Satellite - Export - Shipping Pumps | Tickalara Satellite - Export - Shipping Pumps | 3800 - Tickalara Satellite | KICK EXP 3800-V-021 |  |  | 3800-V-021 | [5 empty] | Managed by Integrity | Managed by Integrity | Managed by Integrity | Managed by Integrity | Managed by Integrity
Parent Asset - Maintenance covered by children_A03 | Tickalara Satellite - Export - Remote Telemetry Unit | Tickalara Satellite - Export - Remote Telemetry Unit | 3800 - Tickalara Satellite | KICK EXP 3800-SAT-EXP-RTU |  |  | 3800-SAT-EXP-RTU | [5 empty] | Maintenance covered by children | Maintenance covered by children | Parent Asset | Parent Asset | Parent Asset
Managed by Integrity_A01 | Tickalara Satellite - Export - Shipping Pumps | Tickalara Satellite - Export - Shipping Pumps | 3800 - Tickalara Satellite | KICK EXP 3800-V-001A |  |  | 3800-V-001A | [5 empty] | Managed by Integrity | Managed by Integrity | Managed by Integrity | Managed by Integrity | Managed by Integrity
Managed by Integrity_A01 | Tickalara Satellite - Export - Shipping Pumps | Tickalara Satellite - Export - Shipping Pumps | 3800 - Tickalara Satellite | KICK EXP 3800-PSV-0001 |  |  | 3800-PSV-0001 | [5 empty] | Managed by Integrity | Managed by Integrity | Managed by Integrity | Managed by Integrity | Managed by Integrity
Managed by Integrity_A01 | Tickalara Satellite - Export - Shipping Pumps | Tickalara Satellite - Export - Shipping Pumps | 3800 - Tickalara Satellite | KICK EXP 3800-PSV-0341 |  |  | 3800-PSV-0341 | [5 empty] | Managed by Integrity | Managed by Integrity | Managed by Integrity | Managed by Integrity | Managed by Integrity
Managed by Integrity_A01 | Tickalara Satellite - Export - Shipping Pumps | Tickalara Satellite - Export - Shipping Pumps | 3800 - Tickalara Satellite | KICK EXP 3800-PSV-0340 |  |  | 3800-PSV-0340 | [5 empty] | Managed by Integrity | Managed by Integrity | Managed by Integrity | Managed by Integrity | Managed by Integrity
Managed by Parent Maintenance_A02 | Tickalara Satellite - Export - Control and Monitor | Tickalara Satellite - Export - Control and Monitor | 3800 - Tickalara Satellite | KICK EXP 3800-PIT-0138 |  |  | 3800-PIT-0138 | [5 empty] | Managed by Parent Maintenance | Managed by Parent Maintenance | Managed by Parent Maintenance | Managed by Parent Maintenance | Managed by Parent Maintenance
Managed by Integrity_A01 | Tickalara Satellite - Export - Shipping Pumps | Tickalara Satellite - Export - Shipping Pumps | 3800 - Tickalara Satellite | KICK EXP 3800-LSHH-0086 |  |  | 3800-LSHH-0086 | [5 empty] | Managed by Integrity | Managed by Integrity | Managed by Integrity | Managed by Integrity | Managed by Integrity
Managed by Integrity_A01 | Tickalara Satellite - Export - Shipping Pumps | Tickalara Satellite - Export - Shipping Pumps | 3800 - Tickalara Satellite | KICK EXP 3800-PSHH-0004 |  |  | 3800-PSHH-0004 | [5 empty] | Managed by Integrity | Managed by Integrity | Managed by Integrity | Managed by Integrity | Managed by Integrity
Managed by Integrity_A01 | Tickalara Satellite - Export - Control and Monitor | Tickalara Satellite - Export - Control and Monitor | 3800 - Tickalara Satellite | KICK EXP 3800-PSV-0130 |  |  | 3800-PSV-0130 | [5 empty] | Managed by Integrity | Managed by Integrity | Managed by Integrity | Managed by Integrity | Managed by Integrity
Managed by Integrity_A01 | Tickalara Satellite - Export - Shipping Pumps | Tickalara Satellite - Export - Shipping Pumps | 3800 - Tickalara Satellite | KICK EXP 3800-PSL-0079 |  |  | 3800-PSL-0079 | [5 empty] | Managed by Integrity | Managed by Integrity | Managed by Integrity | Managed by Integrity | Managed by Integrity
Managed by Parent Maintenance_A02 | Tickalara Satellite - Export - Control and Monitor | Tickalara Satellite - Export - Control and Monitor | 3800 - Tickalara Satellite | KICK EXP 3800-FIT-0128 |  |  | 3800-FIT-0128 | [5 empty] | Managed by Parent Maintenance | Managed by Parent Maintenance | Managed by Parent Maintenance | Managed by Parent Maintenance | Managed by Parent Maintenance
Parent Asset - Maintenance covered by children_A03 | Tickalara Satellite - Export - Shipping Pumps | Tickalara Satellite - Export - Shipping Pumps | 3800 - Tickalara Satellite | KICK EXP 3800-SAT-EXP-PUM |  |  | 3800-SAT-EXP-PUM | [5 empty] | Maintenance covered by children | Maintenance covered by children | Parent Asset | Parent Asset | Parent Asset
Managed by Integrity_A01 | Tickalara Satellite - Export - Shipping Pumps | Tickalara Satellite - Export - Shipping Pumps | 3800 - Tickalara Satellite | KICK EXP 3800-PSV-0002 |  |  | 3800-PSV-0002 | [5 empty] | Managed by Integrity | Managed by Integrity | Managed by Integrity | Managed by Integrity | Managed by Integrity
Parent Asset - Maintenance covered by children_A03 | Tickalara Satellite - Export - Remote Telemetry Unit | Tickalara Satellite - Export - Remote Telemetry Unit | 3800 - Tickalara Satellite | KICK EXP 3800-SAT-EXP-REV |  |  | 3800-SAT-EXP-REV | [5 empty] | Maintenance covered by children | Maintenance covered by children | Parent Asset | Parent Asset | Parent Asset
Managed by Integrity_A01 | Tickalara Satellite - Inlet Manifold - Control and Monitor | Tickalara Satellite - Inlet Manifold - Control and Monitor | 3800 - Tickalara Satellite | KICK INL MAN 3800-PSV-0144 |  |  | 3800-PSV-0144 | [5 empty] | Managed by Integrity | Managed by Integrity | Managed by Integrity | Managed by Integrity | Managed by Integrity
Managed by Integrity_A01 | Tickalara Satellite - Inlet Manifold - Control and Monitor | Tickalara Satellite - Inlet Manifold - Control and Monitor | 3800 - Tickalara Satellite | KICK INL MAN 3800-PSV-0051 |  |  | 3800-PSV-0051 | [5 empty] | Managed by Integrity | Managed by Integrity | Managed by Integrity | Managed by Integrity | Managed by Integrity
Managed by Integrity_A01 | Tickalara Satellite - Inlet Manifold - Control and Monitor | Tickalara Satellite - Inlet Manifold - Control and Monitor | 3800 - Tickalara Satellite | KICK INL MAN 3800-PSV-0037 |  |  | 3800-PSV-0037 | [5 empty] | Managed by Integrity | Managed by Integrity | Managed by Integrity | Managed by Integrity | Managed by Integrity
Managed by Integrity_A01 | Tickalara Satellite - Inlet Manifold - Control and Monitor | Tickalara Satellite - Inlet Manifold - Control and Monitor | 3800 - Tickalara Satellite | KICK INL MAN 3800-PSV-0353 |  |  | 3800-PSV-0353 | [5 empty] | Managed by Integrity | Managed by Integrity | Managed by Integrity | Managed by Integrity | Managed by Integrity
Parent Asset - Maintenance covered by children_A03 | Tickalara Satellite - Inlet Manifold - Control and Monitor | Tickalara Satellite - Inlet Manifold - Control and Monitor | 3800 - Tickalara Satellite | KICK INL MAN 3800-SAT-MAN-CO |  |  | 3800-SAT-MAN-CO | [5 empty] | Maintenance covered by children | Maintenance covered by children | Parent Asset | Parent Asset | Parent Asset
Parent Asset - Maintenance covered by children_A03 | Tickalara Satellite - Inlet Manifold - Control and Monitor | Tickalara Satellite - Inlet Manifold - Control and Monitor | 3800 - Tickalara Satellite | KICK INL MAN 3800-SAT-MAN-BND |  |  | 3800-SAT-MAN-BND | [5 empty] | Maintenance covered by children | Maintenance covered by children | Parent Asset | Parent Asset | Parent Asset
Managed by Integrity_A01 | Tickalara Satellite - Inlet Manifold - Control and Monitor | Tickalara Satellite - Inlet Manifold - Control and Monitor | 3800 - Tickalara Satellite | KICK INL MAN 3800-PSV-0050 |  |  | 3800-PSV-0050 | [5 empty] | Managed by Integrity | Managed by Integrity | Managed by Integrity | Managed by Integrity | Managed by Integrity
Managed by Parent Maintenance_A02 | Tickalara Satellite - Instrument Air - Air Compressor Package - 3800-KX-001 | Tickalara Satellite - Instrument Air - Air Compressor Package - 3800-KX-001 | 3800 - Tickalara Satellite | KICK INST AIR 3800-K-001-EM |  |  | 3800-K-001-EM | [5 empty] | Managed by Parent Maintenance | Managed by Parent Maintenance | Managed by Parent Maintenance | Managed by Parent Maintenance | Managed by Parent Maintenance
Managed by Parent Maintenance_A02 | Tickalara Satellite - Instrument Air - Air Compressor Package - 3800-KX-002 | Tickalara Satellite - Instrument Air - Air Compressor Package - 3800-KX-002 | 3800 - Tickalara Satellite | KICK INST AIR 3800-K-002-EM |  |  | 3800-K-002-EM | [5 empty] | Managed by Parent Maintenance | Managed by Parent Maintenance | Managed by Parent Maintenance | Managed by Parent Maintenance | Managed by Parent Maintenance
Managed by Integrity_A01 | Tickalara Satellite - Instrument Air - Air Compressor Package - 3800-KX-0003 | Tickalara Satellite - Instrument Air - Air Compressor Package - 3800-KX-0003 | 3800 - Tickalara Satellite | KICK INST AIR 3800-V-0003 |  |  | 3800-V-0003 | [5 empty] | Managed by Integrity | Managed by Integrity | Managed by Integrity | Managed by Integrity | Managed by Integrity
Managed by Integrity_A01 | Tickalara Satellite - Instrument Air - Air Compressor Package - 3800-KX-0003 | Tickalara Satellite - Instrument Air - Air Compressor Package - 3800-KX-0003 | 3800 - Tickalara Satellite | KICK INST AIR 3800-PSV-00017 |  |  | 3800-PSV-00017 | [5 empty] | Managed by Integrity | Managed by Integrity | Managed by Integrity | Managed by Integrity | Managed by Integrity
Parent Asset - Maintenance covered by children_A03 | Tickalara Satellite - Instrument Air - Air Compressor Package - 3800-KX-0003 | Tickalara Satellite - Instrument Air - Air Compressor Package - 3800-KX-0003 | 3800 - Tickalara Satellite | KICK INST AIR 3800-KX-0003 |  |  | 3800-KX-0003 | [5 empty] | Maintenance covered by children | Maintenance covered by children | Parent Asset | Parent Asset | Parent Asset
Managed by Integrity_A01 | Tickalara Satellite - Instrument Air - Air Compressor Package - 3800-KX-0003 | Tickalara Satellite - Instrument Air - Air Compressor Package - 3800-KX-0003 | 3800 - Tickalara Satellite | KICK INST AIR 3800-PSV-00017B |  |  | 3800-PSV-00017B | [5 empty] | Managed by Integrity | Managed by Integrity | Managed by Integrity | Managed by Integrity | Managed by Integrity
Managed by Parent Maintenance_A02 | Tickalara Satellite - Instrument Air - Air Compressor Package - 3800-KX-002 | Tickalara Satellite - Instrument Air - Air Compressor Package - 3800-KX-002 | 3800 - Tickalara Satellite | KICK INST AIR 3800-K-002 |  |  | 3800-K-002 | [5 empty] | Managed by Parent Maintenance | Managed by Parent Maintenance | Managed by Parent Maintenance | Managed by Parent Maintenance | Managed by Parent Maintenance
Managed by Parent Maintenance_A02 | Tickalara Satellite - Power Generation - LV Alternator Package - 3800-GX-003 | Tickalara Satellite - Power Generation - LV Alternator Package - 3800-GX-003 | 3800 - Tickalara Satellite | KICK PWR GEN 3800-G-003 |  |  | 3800-G-003 | [5 empty] | Managed by Parent Maintenance | Managed by Parent Maintenance | Managed by Parent Maintenance | Managed by Parent Maintenance | Managed by Parent Maintenance
Managed by Parent Maintenance_A02 | Tickalara Satellite - Power Generation - LV Alternator Package - 3800-GX-003 | Tickalara Satellite - Power Generation - LV Alternator Package - 3800-GX-003 | 3800 - Tickalara Satellite | KICK PWR GEN 3800-DE-029 |  |  | 3800-DE-029 | [5 empty] | Managed by Parent Maintenance | Managed by Parent Maintenance | Managed by Parent Maintenance | Managed by Parent Maintenance | Managed by Parent Maintenance
Managed by Parent Maintenance_A02 | Tickalara Satellite - Power Generation - LV Alternator Package - 3800-GX-003 | Tickalara Satellite - Power Generation - LV Alternator Package - 3800-GX-003 | 3800 - Tickalara Satellite | KICK PWR GEN 3800-G-003-EGMD-2 |  |  | 3800-G-003-EGMD-2 | [5 empty] | Managed by Parent Maintenance | Managed by Parent Maintenance | Managed by Parent Maintenance | Managed by Parent Maintenance | Managed by Parent Maintenance
Managed by Parent Maintenance_A02 | Tickalara Satellite - Power Generation - LV Alternator Package - 3800-GX-002 | Tickalara Satellite - Power Generation - LV Alternator Package - 3800-GX-002 | 3800 - Tickalara Satellite | KICK PWR GEN 3800-DE-028 |  |  | 3800-DE-028 | [5 empty] | Managed by Parent Maintenance | Managed by Parent Maintenance | Managed by Parent Maintenance | Managed by Parent Maintenance | Managed by Parent Maintenance
Managed by Parent Maintenance_A02 | Tickalara Satellite - Power Generation - LV Alternator Package - 3800-GX-002 | Tickalara Satellite - Power Generation - LV Alternator Package - 3800-GX-002 | 3800 - Tickalara Satellite | KICK PWR GEN 3800-G-002 |  |  | 3800-G-002 | [5 empty] | Managed by Parent Maintenance | Managed by Parent Maintenance | Managed by Parent Maintenance | Managed by Parent Maintenance | Managed by Parent Maintenance
Managed by Parent Maintenance_A02 | Tickalara Satellite - Power Generation - LV Alternator Package - 3800-GX-003 | Tickalara Satellite - Power Generation - LV Alternator Package - 3800-GX-003 | 3800 - Tickalara Satellite | KICK PWR GEN 3800-G-003-EDVR-1 |  |  | 3800-G-003-EDVR-1 | [5 empty] | Managed by Parent Maintenance | Managed by Parent Maintenance | Managed by Parent Maintenance | Managed by Parent Maintenance | Managed by Parent Maintenance
Managed by Parent Maintenance_A02 | Tickalara Satellite - Power Generation - LV Alternator Package - 3800-GX-002 | Tickalara Satellite - Power Generation - LV Alternator Package - 3800-GX-002 | 3800 - Tickalara Satellite | KICK PWR GEN 3800-G-002-EGMD-2 |  |  | 3800-G-002-EGMD-2 | [5 empty] | Managed by Parent Maintenance | Managed by Parent Maintenance | Managed by Parent Maintenance | Managed by Parent Maintenance | Managed by Parent Maintenance
Managed by Parent Maintenance_A02 | Tickalara Satellite - Power Generation - LV Alternator Package - 3800-GX-002 | Tickalara Satellite - Power Generation - LV Alternator Package - 3800-GX-002 | 3800 - Tickalara Satellite | KICK PWR GEN 3800-G-002-EDVR-1 |  |  | 3800-G-002-EDVR-1 | [5 empty] | Managed by Parent Maintenance | Managed by Parent Maintenance | Managed by Parent Maintenance | Managed by Parent Maintenance | Managed by Parent Maintenance
Parent Asset - Maintenance covered by children_A03 | Tickalara Satellite - Produced Water Ponds - Interceptor Pond | Tickalara Satellite - Produced Water Ponds - Interceptor Pond | 3800 - Tickalara Satellite | KICK PRO PND 3800-SAT-PRO-INT |  |  | 3800-SAT-PRO-INT | [5 empty] | Maintenance covered by children | Maintenance covered by children | Parent Asset | Parent Asset | Parent Asset
Parent Asset - Maintenance covered by children_A03 | Tickalara Satellite - Produced Water Ponds - Pump-out Pond | Tickalara Satellite - Produced Water Ponds - Pump-out Pond | 3800 - Tickalara Satellite | KICK PRO PND 3800-SAT-PRO-PON-PUM |  |  | 3800-SAT-PRO-PON-PUM | [5 empty] | Maintenance covered by children | Maintenance covered by children | Parent Asset | Parent Asset | Parent Asset
Parent Asset - Maintenance covered by children_A03 | Tickalara Satellite - Produced Water Ponds - Holding Pond | Tickalara Satellite - Produced Water Ponds - Holding Pond | 3800 - Tickalara Satellite | KICK PRO PND 3800-SAT-PRO-HLD-B |  |  | 3800-SAT-PRO-HLD-B | [5 empty] | Maintenance covered by children | Maintenance covered by children | Parent Asset | Parent Asset | Parent Asset
Parent Asset - Maintenance covered by children_A03 | Tickalara Satellite - Produced Water Ponds - Holding Pond | Tickalara Satellite - Produced Water Ponds - Holding Pond | 3800 - Tickalara Satellite | KICK PRO PND 3800-SAT-PRO-HLD-A |  |  | 3800-SAT-PRO-HLD-A | [5 empty] | Maintenance covered by children | Maintenance covered by children | Parent Asset | Parent Asset | Parent Asset
Parent Asset - Maintenance covered by children_A03 | Tickalara Satellite - Produced Water Ponds - Holding Pond | Tickalara Satellite - Produced Water Ponds - Holding Pond | 3800 - Tickalara Satellite | KICK PRO PND 3800-SAT-PRO-HLD |  |  | 3800-SAT-PRO-HLD | [5 empty] | Maintenance covered by children | Maintenance covered by children | Parent Asset | Parent Asset | Parent Asset
Parent Asset - Maintenance covered by children_A03 | Tickalara Satellite - Produced Water Ponds - Interceptor Tanks Bund | Tickalara Satellite - Produced Water Ponds - Interceptor Tanks Bund | 3800 - Tickalara Satellite | KICK PRO PND 3800-SAT-PRO-BND |  |  | 3800-SAT-PRO-BND | [5 empty] | Maintenance covered by children | Maintenance covered by children | Parent Asset | Parent Asset | Parent Asset
Parent Asset - Maintenance covered by children_A03 | Tickalara Satellite - Produced Water Ponds - Pump-out Pond | Tickalara Satellite - Produced Water Ponds - Pump-out Pond | 3800 - Tickalara Satellite | KICK PRO PND 3800-SAT-PRO-PON |  |  | 3800-SAT-PRO-PON | [5 empty] | Maintenance covered by children | Maintenance covered by children | Parent Asset | Parent Asset | Parent Asset

## Sheet2 (hidden)
Satellite | Unit Description | Unit | System Description | System Tag | Column1 | System | Abbrev | Strategy ID | Asset ID
Tickalara Satellite | Export | Tickalara Satellite - Instrument Air | Air Compressor Package | 3800-KX-0003 | 3800-K-0003 | Tickalara Satellite - Instrument Air - Air Compressor Package - 3800-KX-0003 | KICK INST AIR | KICK INST AIR 3800-K-0003
Tickalara Satellite | Export | Tickalara Satellite - Instrument Air | Air Compressor Package | 3800-KX-0003 | 3800-K-0003-EM | Tickalara Satellite - Instrument Air - Air Compressor Package - 3800-KX-0003 | KICK INST AIR | KICK INST AIR 3800-K-0003-EM
Tickalara Satellite | Export | Tickalara Satellite - Instrument Air | Air Compressor Package | 3800-KX-0003 | 3800-PSV-00017 | Tickalara Satellite - Instrument Air - Air Compressor Package - 3800-KX-0003 | KICK INST AIR | KICK INST AIR 3800-PSV-00017
Tickalara Satellite | Export | Tickalara Satellite - Instrument Air | Air Compressor Package | 3800-KX-0003 | 3800-PSV-00017B | Tickalara Satellite - Instrument Air - Air Compressor Package - 3800-KX-0003 | KICK INST AIR | KICK INST AIR 3800-PSV-00017B
Tickalara Satellite | Export | Tickalara Satellite - Instrument Air | Air Compressor Package | 3800-KX-0003 | 3800-V-0003 | Tickalara Satellite - Instrument Air - Air Compressor Package - 3800-KX-0003 | KICK INST AIR | KICK INST AIR 3800-V-0003
Tickalara Satellite | Export | Tickalara Satellite - Instrument Air | Air Compressor Package | 3800-KX-0003 | 3800-KX-0003 | Tickalara Satellite - Instrument Air - Air Compressor Package - 3800-KX-0003 | KICK INST AIR | KICK INST AIR 3800-KX-0003
Tickalara Satellite | Export | Tickalara Satellite - Instrument Air | Air Compressor Package | 3800-KX-001 | 3800-V-001 | Tickalara Satellite - Instrument Air - Air Compressor Package - 3800-KX-001 | KICK INST AIR | KICK INST AIR 3800-V-001
Tickalara Satellite | Export | Tickalara Satellite - Instrument Air | Air Compressor Package | 3800-KX-001 | 3800-K-001 | Tickalara Satellite - Instrument Air - Air Compressor Package - 3800-KX-001 | KICK INST AIR | KICK INST AIR 3800-K-001
Tickalara Satellite | Export | Tickalara Satellite - Instrument Air | Air Compressor Package | 3800-KX-001 | 3800-K-001-EM | Tickalara Satellite - Instrument Air - Air Compressor Package - 3800-KX-001 | KICK INST AIR | KICK INST AIR 3800-K-001-EM
Tickalara Satellite | Export | Tickalara Satellite - Instrument Air | Air Compressor Package | 3800-KX-001 | 3800-KX-001 | Tickalara Satellite - Instrument Air - Air Compressor Package - 3800-KX-001 | KICK INST AIR | KICK INST AIR 3800-KX-001
Tickalara Satellite | Export | Tickalara Satellite - Instrument Air | Air Compressor Package | 3800-KX-002 | 3800-K-002 | Tickalara Satellite - Instrument Air - Air Compressor Package - 3800-KX-002 | KICK INST AIR | KICK INST AIR 3800-K-002
Tickalara Satellite | Export | Tickalara Satellite - Instrument Air | Air Compressor Package | 3800-KX-002 | 3800-K-002-EM | Tickalara Satellite - Instrument Air - Air Compressor Package - 3800-KX-002 | KICK INST AIR | KICK INST AIR 3800-K-002-EM
Tickalara Satellite | Export | Tickalara Satellite - Instrument Air | Air Compressor Package | 3800-KX-002 | 3800-KX-002 | Tickalara Satellite - Instrument Air - Air Compressor Package - 3800-KX-002 | KICK INST AIR | KICK INST AIR 3800-KX-002
Tickalara Satellite | Export | Tickalara Satellite - Instrument Air | Air Compressor Package | 3800-PIT-00342 | 3800-PIT-00342 | Tickalara Satellite - Instrument Air - Air Compressor Package - 3800-PIT-00342 | KICK INST AIR | KICK INST AIR 3800-PIT-00342
Tickalara Satellite | Export | Tickalara Satellite - Buildings | Office | 3800-BLD-001 | 3800-BLD-001-BUFI-1 | Tickalara Satellite - Buildings - Office | KICK BLD | KICK BLD 3800-BLD-001-BUFI-1
Tickalara Satellite | Export | Tickalara Satellite - Buildings | Office | 3800-BLD-001 | 3800-BLD-001-BUFI-2 | Tickalara Satellite - Buildings - Office | KICK BLD | KICK BLD 3800-BLD-001-BUFI-2
Tickalara Satellite | Export | Tickalara Satellite - Buildings | Office | 3800-BLD-001 | 3800-BLD-001-INS | Tickalara Satellite - Buildings - Office | KICK BLD | KICK BLD 3800-BLD-001-INS
Tickalara Satellite | Export | Tickalara Satellite - Buildings | Office | 3800-BLD-001 | 3800-DB-001-CT11 | Tickalara Satellite - Buildings - Office | KICK BLD | KICK BLD 3800-DB-001-CT11
Tickalara Satellite | Export | Tickalara Satellite - Buildings | Office | 3800-BLD-001 | 3800-DB-001-CT7 | Tickalara Satellite - Buildings - Office | KICK BLD | KICK BLD 3800-DB-001-CT7
Tickalara Satellite | Export | Tickalara Satellite - Buildings | Office | 3800-BLD-001 | 3800-DB-001 | Tickalara Satellite - Buildings - Office | KICK BLD | KICK BLD 3800-DB-001
Tickalara Satellite | Export | Tickalara Satellite - Buildings | Office | 3800-BLD-001 | 3800-DB-005-CT5 | Tickalara Satellite - Buildings - Office | KICK BLD | KICK BLD 3800-DB-005-CT5
Tickalara Satellite | Export | Tickalara Satellite - Buildings | Office | 3800-BLD-001 | 3800-DB-005 | Tickalara Satellite - Buildings - Office | KICK BLD | KICK BLD 3800-DB-005
Tickalara Satellite | Export | Tickalara Satellite - Buildings | Office | 3800-BLD-001 | 3800-DB-006-CT6 | Tickalara Satellite - Buildings - Office | KICK BLD | KICK BLD 3800-DB-006-CT6
Tickalara Satellite | Export | Tickalara Satellite - Buildings | Office | 3800-BLD-001 | 3800-DB-006 | Tickalara Satellite - Buildings - Office | KICK BLD | KICK BLD 3800-DB-006
Tickalara Satellite | Export | Tickalara Satellite - Buildings | Office | 3800-BLD-001 | 3800-DB-007-CT7 | Tickalara Satellite - Buildings - Office | KICK BLD | KICK BLD 3800-DB-007-CT7
Tickalara Satellite | Export | Tickalara Satellite - Buildings | Office | 3800-BLD-001 | 3800-DB-007 | Tickalara Satellite - Buildings - Office | KICK BLD | KICK BLD 3800-DB-007
Tickalara Satellite | Export | Tickalara Satellite - Buildings | Office | 3800-BLD-001 | 3800-DB-N10-CT4 | Tickalara Satellite - Buildings - Office | KICK BLD | KICK BLD 3800-DB-N10-CT4
Tickalara Satellite | Export | Tickalara Satellite - Buildings | Office | 3800-BLD-001 | 3800-DB-N10 | Tickalara Satellite - Buildings - Office | KICK BLD | KICK BLD 3800-DB-N10
Tickalara Satellite | Export | Tickalara Satellite - Buildings | Office | 3800-BLD-001 | 3800-DB-N4-CT1 | Tickalara Satellite - Buildings - Office | KICK BLD | KICK BLD 3800-DB-N4-CT1
Tickalara Satellite | Export | Tickalara Satellite - Buildings | Office | 3800-BLD-001 | 3800-DB-N4 | Tickalara Satellite - Buildings - Office | KICK BLD | KICK BLD 3800-DB-N4
Tickalara Satellite | Export | Tickalara Satellite - Buildings | Office | 3800-BLD-001 | 3800-DB-N6-CT2 | Tickalara Satellite - Buildings - Office | KICK BLD | KICK BLD 3800-DB-N6-CT2
Tickalara Satellite | Export | Tickalara Satellite - Buildings | Office | 3800-BLD-001 | 3800-DB-N6 | Tickalara Satellite - Buildings - Office | KICK BLD | KICK BLD 3800-DB-N6
Tickalara Satellite | Export | Tickalara Satellite - Buildings | Office | 3800-BLD-001 | 3800-DB-N8-CT3 | Tickalara Satellite - Buildings - Office | KICK BLD | KICK BLD 3800-DB-N8-CT3
Tickalara Satellite | Export | Tickalara Satellite - Buildings | Office | 3800-BLD-001 | 3800-DB-N8 | Tickalara Satellite - Buildings - Office | KICK BLD | KICK BLD 3800-DB-N8
Tickalara Satellite | Export | Tickalara Satellite - Buildings | Office | 3800-BLD-001 | 3800-BLD-001 | Tickalara Satellite - Buildings - Office | KICK BLD | KICK BLD 3800-BLD-001
Tickalara Satellite | Export | Tickalara Satellite - Buildings | Workshop | 3800-BLD-002 | 3800-DB-002-CT1 | Tickalara Satellite - Buildings - Workshop | KICK BLD | KICK BLD 3800-DB-002-CT1
Tickalara Satellite | Export | Tickalara Satellite - Buildings | Workshop | 3800-BLD-002 | 3800-DB-002 | Tickalara Satellite - Buildings - Workshop | KICK BLD | KICK BLD 3800-DB-002
Tickalara Satellite | Export | Tickalara Satellite - Buildings | Workshop | 3800-BLD-002 | 3800-BLD-002 | Tickalara Satellite - Buildings - Workshop | KICK BLD | KICK BLD 3800-BLD-002
Tickalara Satellite | Export | Tickalara Satellite - Buildings | Workshop | 3800-BLD-003 | 3800-DB-003-CT1 | Tickalara Satellite - Buildings - Workshop | KICK BLD | KICK BLD 3800-DB-003-CT1
Tickalara Satellite | Export | Tickalara Satellite - Buildings | Workshop | 3800-BLD-003 | 3800-DB-003 | Tickalara Satellite - Buildings - Workshop | KICK BLD | KICK BLD 3800-DB-003
Tickalara Satellite | Export | Tickalara Satellite - Buildings | Workshop | 3800-BLD-003 | 3800-BLD-003 | Tickalara Satellite - Buildings - Workshop | KICK BLD | KICK BLD 3800-BLD-003
Tickalara Satellite | Export | Tickalara Satellite - Buildings | Workshop | 3800-BLD-004 | 3800-BLD-004-ALT | Tickalara Satellite - Buildings - Workshop | KICK BLD | KICK BLD 3800-BLD-004-ALT
Tickalara Satellite | Export | Tickalara Satellite - Buildings | Workshop | 3800-BLD-004 | 3800-BLD-004 | Tickalara Satellite - Buildings - Workshop | KICK BLD | KICK BLD 3800-BLD-004
Tickalara Satellite | Export | Tickalara Satellite - Buildings |  | 0 | 3800-SAT-BLD | Tickalara Satellite - Buildings - Office | KICK BLD | KICK BLD 3800-SAT-BLD
Tickalara Satellite | Export | Tickalara Satellite - Export | Flow Meter | 3800-FE-0128 | 3800-FIT-0128 | Tickalara Satellite - Export - Control and Monitor | KICK EXP | KICK EXP 3800-FIT-0128
Tickalara Satellite | Export | Tickalara Satellite - Export | Flow Meter | 3800-FE-0128 | 3800-FE-0128 | Tickalara Satellite - Export - Control and Monitor | KICK EXP | KICK EXP 3800-FE-0128
Tickalara Satellite | Export | Tickalara Satellite - Export | Flow Meter | 3800-FE-0129 | 3800-FIT-0129 | Tickalara Satellite - Export - Control and Monitor | KICK EXP | KICK EXP 3800-FIT-0129
Tickalara Satellite | Export | Tickalara Satellite - Export | Flow Meter | 3800-FE-0129 | 3800-FE-0129 | Tickalara Satellite - Export - Control and Monitor | KICK EXP | KICK EXP 3800-FE-0129
Tickalara Satellite | Export | Tickalara Satellite - Export | Control and Monitor | 3800-PIT-0138 | 3800-PIT-0138 | Tickalara Satellite - Export - Control and Monitor | KICK EXP | KICK EXP 3800-PIT-0138
Tickalara Satellite | Export | Tickalara Satellite - Export | Control and Monitor | 3800-PSV-0130 | 3800-PSV-0130 | Tickalara Satellite - Export - Control and Monitor | KICK EXP | KICK EXP 3800-PSV-0130
Tickalara Satellite | Export | Tickalara Satellite - Export | Shipping Pumps | 3800-SAT-EXP-PUM | 3800-PSV-0340 | Tickalara Satellite - Export - Shipping Pumps | KICK EXP | KICK EXP 3800-PSV-0340
Tickalara Satellite | Export | Tickalara Satellite - Export | Shipping Pumps | 3800-SAT-EXP-PUM | 3800-V-001A | Tickalara Satellite - Export - Shipping Pumps | KICK EXP | KICK EXP 3800-V-001A
Tickalara Satellite | Export | Tickalara Satellite - Export | Shipping Pumps | 3800-SAT-EXP-PUM | 3800-PSV-0341 | Tickalara Satellite - Export - Shipping Pumps | KICK EXP | KICK EXP 3800-PSV-0341
Tickalara Satellite | Export | Tickalara Satellite - Export | Shipping Pumps | 3800-SAT-EXP-PUM | 3800-V-001B | Tickalara Satellite - Export - Shipping Pumps | KICK EXP | KICK EXP 3800-V-001B
Tickalara Satellite | Export | Tickalara Satellite - Export | Shipping Pumps | 3800-SAT-EXP-PUM | 3800-P-001-AIR | Tickalara Satellite - Export - Shipping Pumps | KICK EXP | KICK EXP 3800-P-001-AIR
Tickalara Satellite | Export | Tickalara Satellite - Export | Shipping Pumps | 3800-SAT-EXP-PUM | 3800-DE-002A | Tickalara Satellite - Export - Shipping Pumps | KICK EXP | KICK EXP 3800-DE-002A
Tickalara Satellite | Export | Tickalara Satellite - Export | Shipping Pumps | 3800-SAT-EXP-PUM | 3800-P-002A | Tickalara Satellite - Export - Shipping Pumps | KICK EXP | KICK EXP 3800-P-002A
Tickalara Satellite | Export | Tickalara Satellite - Export | Shipping Pumps | 3800-SAT-EXP-PUM | 3800-PX-002A | Tickalara Satellite - Export - Shipping Pumps | KICK EXP | KICK EXP 3800-PX-002A
Tickalara Satellite | Export | Tickalara Satellite - Export | Shipping Pumps | 3800-SAT-EXP-PUM | 3800-DE-002B | Tickalara Satellite - Export - Shipping Pumps | KICK EXP | KICK EXP 3800-DE-002B
Tickalara Satellite | Export | Tickalara Satellite - Export | Shipping Pumps | 3800-SAT-EXP-PUM | 3800-P-002B | Tickalara Satellite - Export - Shipping Pumps | KICK EXP | KICK EXP 3800-P-002B
Tickalara Satellite | Export | Tickalara Satellite - Export | Shipping Pumps | 3800-SAT-EXP-PUM | 3800-PX-002B | Tickalara Satellite - Export - Shipping Pumps | KICK EXP | KICK EXP 3800-PX-002B
Tickalara Satellite | Export | Tickalara Satellite - Export | Shipping Pumps | 3800-SAT-EXP-PUM | 3800-P-001-CHA | Tickalara Satellite - Export - Shipping Pumps | KICK EXP | KICK EXP 3800-P-001-CHA
Tickalara Satellite | Export | Tickalara Satellite - Export | Shipping Pumps | 3800-SAT-EXP-PUM | 3800-P-001-FUE-BND | Tickalara Satellite - Export - Shipping Pumps | KICK EXP | KICK EXP 3800-P-001-FUE-BND
Tickalara Satellite | Export | Tickalara Satellite - Export | Shipping Pumps | 3800-SAT-EXP-PUM | 3800-TK-007 | Tickalara Satellite - Export - Shipping Pumps | KICK EXP | KICK EXP 3800-TK-007
Tickalara Satellite | Export | Tickalara Satellite - Export | Shipping Pumps | 3800-SAT-EXP-PUM | 3800-TK-008 | Tickalara Satellite - Export - Shipping Pumps | KICK EXP | KICK EXP 3800-TK-008
Tickalara Satellite | Export | Tickalara Satellite - Export | Shipping Pumps | 3800-SAT-EXP-PUM | 3800-P-001-FUE | Tickalara Satellite - Export - Shipping Pumps | KICK EXP | KICK EXP 3800-P-001-FUE
Tickalara Satellite | Export | Tickalara Satellite - Export | Shipping Pumps | 3800-SAT-EXP-PUM | 3800-PSHH-0004 | Tickalara Satellite - Export - Shipping Pumps | KICK EXP | KICK EXP 3800-PSHH-0004
Tickalara Satellite | Export | Tickalara Satellite - Export | Shipping Pumps | 3800-SAT-EXP-PUM | 3800-PSL-0079 | Tickalara Satellite - Export - Shipping Pumps | KICK EXP | KICK EXP 3800-PSL-0079
Tickalara Satellite | Export | Tickalara Satellite - Export | Shipping Pumps | 3800-SAT-EXP-PUM | 3800-PSLL-0004 | Tickalara Satellite - Export - Shipping Pumps | KICK EXP | KICK EXP 3800-PSLL-0004
Tickalara Satellite | Export | Tickalara Satellite - Export | Shipping Pumps | 3800-SAT-EXP-PUM | 3800-PSV-0001 | Tickalara Satellite - Export - Shipping Pumps | KICK EXP | KICK EXP 3800-PSV-0001
Tickalara Satellite | Export | Tickalara Satellite - Export | Shipping Pumps | 3800-SAT-EXP-PUM | 3800-P-001A | Tickalara Satellite - Export - Shipping Pumps | KICK EXP | KICK EXP 3800-P-001A
Tickalara Satellite | Export | Tickalara Satellite - Export | Shipping Pumps | 3800-SAT-EXP-PUM | 3800-P-001A-DE | Tickalara Satellite - Export - Shipping Pumps | KICK EXP | KICK EXP 3800-P-001A-DE
Tickalara Satellite | Export | Tickalara Satellite - Export | Shipping Pumps | 3800-SAT-EXP-PUM | 3800-PSL-0080 | Tickalara Satellite - Export - Shipping Pumps | KICK EXP | KICK EXP 3800-PSL-0080
Tickalara Satellite | Export | Tickalara Satellite - Export | Shipping Pumps | 3800-SAT-EXP-PUM | 3800-V-018 | Tickalara Satellite - Export - Shipping Pumps | KICK EXP | KICK EXP 3800-V-018
Tickalara Satellite | Inlet Manifold | Tickalara Satellite - Export | Shipping Pumps | 3800-SAT-EXP-PUM | 3800-V-019 | Tickalara Satellite - Export - Shipping Pumps | KICK EXP | KICK EXP 3800-V-019
Tickalara Satellite | Inlet Manifold | Tickalara Satellite - Export | Shipping Pumps | 3800-SAT-EXP-PUM | 3800-PX-001A | Tickalara Satellite - Export - Shipping Pumps | KICK EXP | KICK EXP 3800-PX-001A
Tickalara Satellite | Inlet Manifold | Tickalara Satellite - Export | Shipping Pumps | 3800-SAT-EXP-PUM | 3800-PSV-0002 | Tickalara Satellite - Export - Shipping Pumps | KICK EXP | KICK EXP 3800-PSV-0002
Tickalara Satellite | Inlet Manifold | Tickalara Satellite - Export | Shipping Pumps | 3800-SAT-EXP-PUM | 3800-P-001B | Tickalara Satellite - Export - Shipping Pumps | KICK EXP | KICK EXP 3800-P-001B
Tickalara Satellite | Inlet Manifold | Tickalara Satellite - Export | Shipping Pumps | 3800-SAT-EXP-PUM | 3800-P-001B-DE | Tickalara Satellite - Export - Shipping Pumps | KICK EXP | KICK EXP 3800-P-001B-DE
Tickalara Satellite | Inlet Manifold | Tickalara Satellite - Export | Shipping Pumps | 3800-SAT-EXP-PUM | 3800-PSL-0081 | Tickalara Satellite - Export - Shipping Pumps | KICK EXP | KICK EXP 3800-PSL-0081
Tickalara Satellite | Inlet Manifold | Tickalara Satellite - Export | Shipping Pumps | 3800-SAT-EXP-PUM | 3800-V-020 | Tickalara Satellite - Export - Shipping Pumps | KICK EXP | KICK EXP 3800-V-020
Tickalara Satellite | Inlet Manifold | Tickalara Satellite - Export | Shipping Pumps | 3800-SAT-EXP-PUM | 3800-V-021 | Tickalara Satellite - Export - Shipping Pumps | KICK EXP | KICK EXP 3800-V-021
Tickalara Satellite | Inlet Manifold | Tickalara Satellite - Export | Shipping Pumps | 3800-SAT-EXP-PUM | 3800-PX-001B | Tickalara Satellite - Export - Shipping Pumps | KICK EXP | KICK EXP 3800-PX-001B
Tickalara Satellite | Inlet Manifold | Tickalara Satellite - Export | Shipping Pumps | 3800-SAT-EXP-PUM | 3800-SAT-EXP-PUM-BND | Tickalara Satellite - Export - Shipping Pumps | KICK EXP | KICK EXP 3800-SAT-EXP-PUM-BND
Tickalara Satellite | Inlet Manifold | Tickalara Satellite - Export | Shipping Pumps | 3800-SAT-EXP-PUM | 3800-LSHH-0086 | Tickalara Satellite - Export - Shipping Pumps | KICK EXP | KICK EXP 3800-LSHH-0086
Tickalara Satellite | Inlet Manifold | Tickalara Satellite - Export | Shipping Pumps | 3800-SAT-EXP-PUM | 3800-P-006 | Tickalara Satellite - Export - Shipping Pumps | KICK EXP | KICK EXP 3800-P-006
Tickalara Satellite | Inlet Manifold | Tickalara Satellite - Export | Shipping Pumps | 3800-SAT-EXP-PUM | 3800-TK-004 | Tickalara Satellite - Export - Shipping Pumps | KICK EXP | KICK EXP 3800-TK-004
Tickalara Satellite | Inlet Manifold | Tickalara Satellite - Export | Shipping Pumps | 3800-SAT-EXP-PUM | 3800-SAT-EXP-PUM | Tickalara Satellite - Export - Shipping Pumps | KICK EXP | KICK EXP 3800-SAT-EXP-PUM
Tickalara Satellite | Inlet Manifold | Tickalara Satellite - Export | Remote Telemetry Unit | 3800-SAT-EXP-REV | 3800-SAT-EXP-REV | Tickalara Satellite - Export - Remote Telemetry Unit | KICK EXP | KICK EXP 3800-SAT-EXP-REV
Tickalara Satellite | Inlet Manifold | Tickalara Satellite - Export | Remote Telemetry Unit | 3800-SAT-EXP-RTU | 3800-SAT-EXP-RTU | Tickalara Satellite - Export - Remote Telemetry Unit | KICK EXP | KICK EXP 3800-SAT-EXP-RTU
Tickalara Satellite | Inlet Manifold | Tickalara Satellite - Export | Discharge to JMOP Shutdown Valve | 3800-XSV-0127 | 3800-XSV-0127-VAAC-2 | Tickalara Satellite - Export - Discharge to JMOP Shutdown Valve | KICK EXP | KICK EXP 3800-XSV-0127-VAAC-2
Tickalara Satellite | Inlet Manifold | Tickalara Satellite - Export | Discharge to JMOP Shutdown Valve | 3800-XSV-0127 | 3800-XSV-0127-VABA-1 | Tickalara Satellite - Export - Discharge to JMOP Shutdown Valve | KICK EXP | KICK EXP 3800-XSV-0127-VABA-1
Tickalara Satellite | Inlet Manifold | Tickalara Satellite - Export | Discharge to JMOP Shutdown Valve | 3800-XSV-0127 | 3800-XY-0127 | Tickalara Satellite - Export - Discharge to JMOP Shutdown Valve | KICK EXP | KICK EXP 3800-XY-0127
Tickalara Satellite | Inlet Manifold | Tickalara Satellite - Export | Discharge to JMOP Shutdown Valve | 3800-XSV-0127 | 3800-ZSC-0127 | Tickalara Satellite - Export - Discharge to JMOP Shutdown Valve | KICK EXP | KICK EXP 3800-ZSC-0127
Tickalara Satellite | Evaporation Ponds | Tickalara Satellite - Export | Discharge to JMOP Shutdown Valve | 3800-XSV-0127 | 3800-ZSO-0127 | Tickalara Satellite - Export - Discharge to JMOP Shutdown Valve | KICK EXP | KICK EXP 3800-ZSO-0127
Tickalara Satellite | Produced Water Ponds | Tickalara Satellite - Export | Discharge to JMOP Shutdown Valve | 3800-XSV-0127 | 3800-XSV-0127 | Tickalara Satellite - Export - Discharge to JMOP Shutdown Valve | KICK EXP | KICK EXP 3800-XSV-0127
Tickalara Satellite | Produced Water Ponds | Tickalara Satellite - Inlet Manifold | Control and Monitor | 3800-PSV-0050 | 3800-PSV-0050 | Tickalara Satellite - Inlet Manifold - Control and Monitor | KICK INL MAN | KICK INL MAN 3800-PSV-0050
Tickalara Satellite | Produced Water Ponds | Tickalara Satellite - Inlet Manifold | Control and Monitor | 3800-PSV-0051 | 3800-PSV-0051 | Tickalara Satellite - Inlet Manifold - Control and Monitor | KICK INL MAN | KICK INL MAN 3800-PSV-0051
Tickalara Satellite | Produced Water Ponds | Tickalara Satellite - Inlet Manifold | Control and Monitor | 3800-SAT-MAN-BND | 3800-SAT-MAN-BND | Tickalara Satellite - Inlet Manifold - Control and Monitor | KICK INL MAN | KICK INL MAN 3800-SAT-MAN-BND
Tickalara Satellite | Produced Water Ponds | Tickalara Satellite - Inlet Manifold | Control and Monitor | 3800-SAT-MAN-CO | 3800-PSV-0037 | Tickalara Satellite - Inlet Manifold - Control and Monitor | KICK INL MAN | KICK INL MAN 3800-PSV-0037
Tickalara Satellite | Produced Water Ponds | Tickalara Satellite - Inlet Manifold | Control and Monitor | 3800-SAT-MAN-CO | 3800-PSV-0144 | Tickalara Satellite - Inlet Manifold - Control and Monitor | KICK INL MAN | KICK INL MAN 3800-PSV-0144
Tickalara Satellite | Produced Water Ponds | Tickalara Satellite - Inlet Manifold | Control and Monitor | 3800-SAT-MAN-CO | 3800-PSV-0353 | Tickalara Satellite - Inlet Manifold - Control and Monitor | KICK INL MAN | KICK INL MAN 3800-PSV-0353
Tickalara Satellite | Produced Water Ponds | Tickalara Satellite - Inlet Manifold | Control and Monitor | 3800-SAT-MAN-CO | 3800-SAT-MAN-CO | Tickalara Satellite - Inlet Manifold - Control and Monitor | KICK INL MAN | KICK INL MAN 3800-SAT-MAN-CO
Tickalara Satellite | Power Generation | Tickalara Satellite - Inlet Manifold | Shutdown Valve | 3800-XV-0053 | 3800-XY-0053 | Tickalara Satellite - Inlet Manifold - Shutdown Valve | KICK INL MAN | KICK INL MAN 3800-XY-0053
Tickalara Satellite | Power Generation | Tickalara Satellite - Inlet Manifold | Shutdown Valve | 3800-XV-0053 | 3800-ZT-0053 | Tickalara Satellite - Inlet Manifold - Shutdown Valve | KICK INL MAN | KICK INL MAN 3800-ZT-0053
Tickalara Satellite | Power Generation | Tickalara Satellite - Inlet Manifold | Shutdown Valve | 3800-XV-0053 | 3800-XV-0053 | Tickalara Satellite - Inlet Manifold - Shutdown Valve | KICK INL MAN | KICK INL MAN 3800-XV-0053
Tickalara Satellite | Power Generation | Tickalara Satellite - Inlet Manifold | Shutdown Valve | 3800-XV-0055 | 3800-HS-0055 | Tickalara Satellite - Inlet Manifold - Shutdown Valve | KICK INL MAN | KICK INL MAN 3800-HS-0055
Tickalara Satellite | Power Generation | Tickalara Satellite - Inlet Manifold | Shutdown Valve | 3800-XV-0055 | 3800-XY-0055 | Tickalara Satellite - Inlet Manifold - Shutdown Valve | KICK INL MAN | KICK INL MAN 3800-XY-0055
Tickalara Satellite | Power Generation | Tickalara Satellite - Inlet Manifold | Shutdown Valve | 3800-XV-0055 | 3800-XY-0055A | Tickalara Satellite - Inlet Manifold - Shutdown Valve | KICK INL MAN | KICK INL MAN 3800-XY-0055A
Tickalara Satellite | Power Generation | Tickalara Satellite - Inlet Manifold | Shutdown Valve | 3800-XV-0055 | 3800-XV-0055 | Tickalara Satellite - Inlet Manifold - Shutdown Valve | KICK INL MAN | KICK INL MAN 3800-XV-0055
Tickalara Satellite | Power Generation | Tickalara Satellite - Produced Water Ponds | Interceptor Tanks Bund | 3800-SAT-PRO-BND | 3800-SAT-PRO-BND | Tickalara Satellite - Produced Water Ponds - Interceptor Tanks Bund | KICK PRO PND | KICK PRO PND 3800-SAT-PRO-BND
Tickalara Satellite | Power Generation | Tickalara Satellite - Produced Water Ponds | Holding Pond | 3800-SAT-PRO-HLD | 3800-SAT-PRO-HLD-A | Tickalara Satellite - Produced Water Ponds - Holding Pond | KICK PRO PND | KICK PRO PND 3800-SAT-PRO-HLD-A
Tickalara Satellite | Power Generation | Tickalara Satellite - Produced Water Ponds | Holding Pond | 3800-SAT-PRO-HLD | 3800-SAT-PRO-HLD-B | Tickalara Satellite - Produced Water Ponds - Holding Pond | KICK PRO PND | KICK PRO PND 3800-SAT-PRO-HLD-B
Tickalara Satellite | Power Generation | Tickalara Satellite - Produced Water Ponds | Holding Pond | 3800-SAT-PRO-HLD | 3800-SAT-PRO-HLD | Tickalara Satellite - Produced Water Ponds - Holding Pond | KICK PRO PND | KICK PRO PND 3800-SAT-PRO-HLD
Tickalara Satellite | Power Generation | Tickalara Satellite - Produced Water Ponds | Interceptor Pond | 3800-SAT-PRO-INT | 3800-P-004 | Tickalara Satellite - Produced Water Ponds - Interceptor Pond | KICK PRO PND | KICK PRO PND 3800-P-004
Tickalara Satellite | Power Generation | Tickalara Satellite - Produced Water Ponds | Interceptor Pond | 3800-SAT-PRO-INT | 3800-SAT-PRO-INT | Tickalara Satellite - Produced Water Ponds - Interceptor Pond | KICK PRO PND | KICK PRO PND 3800-SAT-PRO-INT
Tickalara Satellite | Power Generation | Tickalara Satellite - Produced Water Ponds | Pump-out Pond | 3800-SAT-PRO-PON | 3800-SAT-PRO-PON-PUM | Tickalara Satellite - Produced Water Ponds - Pump-out Pond | KICK PRO PND | KICK PRO PND 3800-SAT-PRO-PON-PUM
Tickalara Satellite | Crude Oil Storage | Tickalara Satellite - Produced Water Ponds | Pump-out Pond | 3800-SAT-PRO-PON | 3800-SAT-PRO-PON | Tickalara Satellite - Produced Water Ponds - Pump-out Pond | KICK PRO PND | KICK PRO PND 3800-SAT-PRO-PON
Tickalara Satellite | Crude Oil Storage | Tickalara Satellite - Power Generation | LV Alternator Package | 3800-GX-002 | 3800-DE-028 | Tickalara Satellite - Power Generation - LV Alternator Package - 3800-GX-002 | KICK PWR GEN | KICK PWR GEN 3800-DE-028
Tickalara Satellite | Crude Oil Storage | Tickalara Satellite - Power Generation | LV Alternator Package | 3800-GX-002 | 3800-G-002-EDVR-1 | Tickalara Satellite - Power Generation - LV Alternator Package - 3800-GX-002 | KICK PWR GEN | KICK PWR GEN 3800-G-002-EDVR-1
Tickalara Satellite | Crude Oil Storage | Tickalara Satellite - Power Generation | LV Alternator Package | 3800-GX-002 | 3800-G-002-EGMD-2 | Tickalara Satellite - Power Generation - LV Alternator Package - 3800-GX-002 | KICK PWR GEN | KICK PWR GEN 3800-G-002-EGMD-2
Tickalara Satellite | Crude Oil Storage | Tickalara Satellite - Power Generation | LV Alternator Package | 3800-GX-002 | 3800-G-002 | Tickalara Satellite - Power Generation - LV Alternator Package - 3800-GX-002 | KICK PWR GEN | KICK PWR GEN 3800-G-002
Tickalara Satellite | Crude Oil Storage | Tickalara Satellite - Power Generation | LV Alternator Package | 3800-GX-002 | 3800-GX-002 | Tickalara Satellite - Power Generation - LV Alternator Package - 3800-GX-002 | KICK PWR GEN | KICK PWR GEN 3800-GX-002
Tickalara Satellite | Crude Oil Storage | Tickalara Satellite - Power Generation | LV Alternator Package | 3800-GX-003 | 3800-DE-029 | Tickalara Satellite - Power Generation - LV Alternator Package - 3800-GX-003 | KICK PWR GEN | KICK PWR GEN 3800-DE-029
Tickalara Satellite | Crude Oil Storage | Tickalara Satellite - Power Generation | LV Alternator Package | 3800-GX-003 | 3800-G-003-EDVR-1 | Tickalara Satellite - Power Generation - LV Alternator Package - 3800-GX-003 | KICK PWR GEN | KICK PWR GEN 3800-G-003-EDVR-1
Tickalara Satellite | Crude Oil Storage | Tickalara Satellite - Power Generation | LV Alternator Package | 3800-GX-003 | 3800-G-003-EGMD-2 | Tickalara Satellite - Power Generation - LV Alternator Package - 3800-GX-003 | KICK PWR GEN | KICK PWR GEN 3800-G-003-EGMD-2
Tickalara Satellite | Crude Oil Storage | Tickalara Satellite - Power Generation | LV Alternator Package | 3800-GX-003 | 3800-G-003 | Tickalara Satellite - Power Generation - LV Alternator Package - 3800-GX-003 | KICK PWR GEN | KICK PWR GEN 3800-G-003
Tickalara Satellite | Crude Oil Storage | Tickalara Satellite - Power Generation | LV Alternator Package | 3800-GX-003 | 3800-GX-003 | Tickalara Satellite - Power Generation - LV Alternator Package - 3800-GX-003 | KICK PWR GEN | KICK PWR GEN 3800-GX-003
Tickalara Satellite | Crude Oil Storage | Tickalara Satellite - Power Generation | Tank Diesel Fuel | 3800-TK-0073 | 3800-TK-0073 | Tickalara Satellite - Power Generation - Tank Diesel Fuel | KICK PWR GEN | KICK PWR GEN 3800-TK-0073
Tickalara Satellite | Crude Oil Storage | Tickalara Satellite - Crude Oil Storage | Tank Farm Bund | 3800-SAT-STO-BND | 3800-SAT-STO-BND | Tickalara Satellite - Crude Oil Storage - Tank Farm Bund | KICK CRUDE OIL STRG | KICK CRUDE OIL STRG 3800-SAT-STO-BND
Tickalara Satellite | Crude Oil Storage | Tickalara Satellite - Crude Oil Storage | Dewatering / Test Tanks | 3800-SAT-STO-DEW | 3800-DE-003 | Tickalara Satellite - Crude Oil Storage - Dewatering / Test Tanks | KICK CRUDE OIL STRG | KICK CRUDE OIL STRG 3800-DE-003
Tickalara Satellite | Crude Oil Storage | Tickalara Satellite - Crude Oil Storage | Dewatering / Test Tanks | 3800-SAT-STO-DEW | 3800-P-003 | Tickalara Satellite - Crude Oil Storage - Dewatering / Test Tanks | KICK CRUDE OIL STRG | KICK CRUDE OIL STRG 3800-P-003
Tickalara Satellite | Crude Oil Storage | Tickalara Satellite - Crude Oil Storage | Dewatering / Test Tanks | 3800-SAT-STO-DEW | 3800-PX-003-BND | Tickalara Satellite - Crude Oil Storage - Dewatering / Test Tanks | KICK CRUDE OIL STRG | KICK CRUDE OIL STRG 3800-PX-003-BND
Tickalara Satellite | Crude Oil Storage | Tickalara Satellite - Crude Oil Storage | Dewatering / Test Tanks | 3800-SAT-STO-DEW | 3800-PX-003 | Tickalara Satellite - Crude Oil Storage - Dewatering / Test Tanks | KICK CRUDE OIL STRG | KICK CRUDE OIL STRG 3800-PX-003
Tickalara Satellite | Crude Oil Storage | Tickalara Satellite - Crude Oil Storage | Dewatering / Test Tanks | 3800-SAT-STO-DEW | 3800-SAT-STO-CHEM-BND | Tickalara Satellite - Crude Oil Storage - Dewatering / Test Tanks | KICK CRUDE OIL STRG | KICK CRUDE OIL STRG 3800-SAT-STO-CHEM-BND
Tickalara Satellite | Crude Oil Storage | Tickalara Satellite - Crude Oil Storage | Dewatering / Test Tanks | 3800-SAT-STO-DEW | 3800-TK-001A | Tickalara Satellite - Crude Oil Storage - Dewatering / Test Tanks | KICK CRUDE OIL STRG | KICK CRUDE OIL STRG 3800-TK-001A
Tickalara Satellite | Crude Oil Storage | Tickalara Satellite - Crude Oil Storage | Dewatering / Test Tanks | 3800-SAT-STO-DEW | 3800-TK-001B | Tickalara Satellite - Crude Oil Storage - Dewatering / Test Tanks | KICK CRUDE OIL STRG | KICK CRUDE OIL STRG 3800-TK-001B
Tickalara Satellite | Crude Oil Storage | Tickalara Satellite - Crude Oil Storage | Dewatering / Test Tanks | 3800-SAT-STO-DEW | 3800-TK-001C | Tickalara Satellite - Crude Oil Storage - Dewatering / Test Tanks | KICK CRUDE OIL STRG | KICK CRUDE OIL STRG 3800-TK-001C
Tickalara Satellite | Crude Oil Storage | Tickalara Satellite - Crude Oil Storage | Dewatering / Test Tanks | 3800-SAT-STO-DEW | 3800-LSHH-0055 | Tickalara Satellite - Crude Oil Storage - Dewatering / Test Tanks | KICK CRUDE OIL STRG | KICK CRUDE OIL STRG 3800-LSHH-0055
Tickalara Satellite | Crude Oil Storage | Tickalara Satellite - Crude Oil Storage | Dewatering / Test Tanks | 3800-SAT-STO-DEW | 3800-TK-003-CO | Tickalara Satellite - Crude Oil Storage - Dewatering / Test Tanks | KICK CRUDE OIL STRG | KICK CRUDE OIL STRG 3800-TK-003-CO
Tickalara Satellite | Crude Oil Storage | Tickalara Satellite - Crude Oil Storage | Dewatering / Test Tanks | 3800-SAT-STO-DEW | 3800-TK-003 | Tickalara Satellite - Crude Oil Storage - Dewatering / Test Tanks | KICK CRUDE OIL STRG | KICK CRUDE OIL STRG 3800-TK-003
Tickalara Satellite | Crude Oil Storage | Tickalara Satellite - Crude Oil Storage | Dewatering / Test Tanks | 3800-SAT-STO-DEW | 3800-SAT-STO-DEW | Tickalara Satellite - Crude Oil Storage - Dewatering / Test Tanks | KICK CRUDE OIL STRG | KICK CRUDE OIL STRG 3800-SAT-STO-DEW
Tickalara Satellite | Crude Oil Storage | Tickalara Satellite - Crude Oil Storage | Production Tanks | 3800-SAT-STO-PRO | 3800-LSH-0087 | Tickalara Satellite - Crude Oil Storage - Production Tanks | KICK CRUDE OIL STRG | KICK CRUDE OIL STRG 3800-LSH-0087
Tickalara Satellite | Crude Oil Storage | Tickalara Satellite - Crude Oil Storage | Production Tanks | 3800-SAT-STO-PRO | 3800-LSHH-0261 | Tickalara Satellite - Crude Oil Storage - Production Tanks | KICK CRUDE OIL STRG | KICK CRUDE OIL STRG 3800-LSHH-0261
Tickalara Satellite | Crude Oil Storage | Tickalara Satellite - Crude Oil Storage | Production Tanks | 3800-SAT-STO-PRO | 3800-TK-003A-CO | Tickalara Satellite - Crude Oil Storage - Production Tanks | KICK CRUDE OIL STRG | KICK CRUDE OIL STRG 3800-TK-003A-CO
Tickalara Satellite | Crude Oil Storage | Tickalara Satellite - Crude Oil Storage | Production Tanks | 3800-SAT-STO-PRO | 3800-TK-003A | Tickalara Satellite - Crude Oil Storage - Production Tanks | KICK CRUDE OIL STRG | KICK CRUDE OIL STRG 3800-TK-003A
Tickalara Satellite | Crude Oil Storage | Tickalara Satellite - Crude Oil Storage | Production Tanks | 3800-SAT-STO-PRO | 3800-LIT-0088 | Tickalara Satellite - Crude Oil Storage - Production Tanks | KICK CRUDE OIL STRG | KICK CRUDE OIL STRG 3800-LIT-0088
Tickalara Satellite | Crude Oil Storage | Tickalara Satellite - Crude Oil Storage | Production Tanks | 3800-SAT-STO-PRO | 3800-TK-003B-CO | Tickalara Satellite - Crude Oil Storage - Production Tanks | KICK CRUDE OIL STRG | KICK CRUDE OIL STRG 3800-TK-003B-CO
Tickalara Satellite | Crude Oil Storage | Tickalara Satellite - Crude Oil Storage | Production Tanks | 3800-SAT-STO-PRO | 3800-TK-003B | Tickalara Satellite - Crude Oil Storage - Production Tanks | KICK CRUDE OIL STRG | KICK CRUDE OIL STRG 3800-TK-003B
Tickalara Satellite | Crude Oil Storage | Tickalara Satellite - Crude Oil Storage | Production Tanks | 3800-SAT-STO-PRO | 3800-TK-003C | Tickalara Satellite - Crude Oil Storage - Production Tanks | KICK CRUDE OIL STRG | KICK CRUDE OIL STRG 3800-TK-003C
Tickalara Satellite | Crude Oil Storage | Tickalara Satellite - Crude Oil Storage | Production Tanks | 3800-SAT-STO-PRO | 3800-TK-003D-CO | Tickalara Satellite - Crude Oil Storage - Production Tanks | KICK CRUDE OIL STRG | KICK CRUDE OIL STRG 3800-TK-003D-CO
Tickalara Satellite | Crude Oil Storage | Tickalara Satellite - Crude Oil Storage | Production Tanks | 3800-SAT-STO-PRO | 3800-TK-003D | Tickalara Satellite - Crude Oil Storage - Production Tanks | KICK CRUDE OIL STRG | KICK CRUDE OIL STRG 3800-TK-003D
Tickalara Satellite | Crude Oil Storage | Tickalara Satellite - Crude Oil Storage | Production Tanks | 3800-SAT-STO-PRO | 3800-LIC-0059 | Tickalara Satellite - Crude Oil Storage - Production Tanks | KICK CRUDE OIL STRG | KICK CRUDE OIL STRG 3800-LIC-0059
Tickalara Satellite | Crude Oil Storage | Tickalara Satellite - Crude Oil Storage | Production Tanks | 3800-SAT-STO-PRO | 3800-LSHH-0053 | Tickalara Satellite - Crude Oil Storage - Production Tanks | KICK CRUDE OIL STRG | KICK CRUDE OIL STRG 3800-LSHH-0053
Tickalara Satellite | Crude Oil Storage | Tickalara Satellite - Crude Oil Storage | Production Tanks | 3800-SAT-STO-PRO | 3800-LSLL-0004 | Tickalara Satellite - Crude Oil Storage - Production Tanks | KICK CRUDE OIL STRG | KICK CRUDE OIL STRG 3800-LSLL-0004
Tickalara Satellite | Crude Oil Storage | Tickalara Satellite - Crude Oil Storage | Production Tanks | 3800-SAT-STO-PRO | 3800-TK-003E-CO | Tickalara Satellite - Crude Oil Storage - Production Tanks | KICK CRUDE OIL STRG | KICK CRUDE OIL STRG 3800-TK-003E-CO
Tickalara Satellite | Crude Oil Storage | Tickalara Satellite - Crude Oil Storage | Production Tanks | 3800-SAT-STO-PRO | 3800-TK-003E | Tickalara Satellite - Crude Oil Storage - Production Tanks | KICK CRUDE OIL STRG | KICK CRUDE OIL STRG 3800-TK-003E
Tickalara Satellite | Crude Oil Storage | Tickalara Satellite - Crude Oil Storage | Production Tanks | 3800-SAT-STO-PRO | 3800-LIT-0344 | Tickalara Satellite - Crude Oil Storage - Production Tanks | KICK CRUDE OIL STRG | KICK CRUDE OIL STRG 3800-LIT-0344
Tickalara Satellite | Crude Oil Storage | Tickalara Satellite - Crude Oil Storage | Production Tanks | 3800-SAT-STO-PRO | 3800-LSHH-0345 | Tickalara Satellite - Crude Oil Storage - Production Tanks | KICK CRUDE OIL STRG | KICK CRUDE OIL STRG 3800-LSHH-0345
Tickalara Satellite | Crude Oil Storage | Tickalara Satellite - Crude Oil Storage | Production Tanks | 3800-SAT-STO-PRO | 3800-TK-048 | Tickalara Satellite - Crude Oil Storage - Production Tanks | KICK CRUDE OIL STRG | KICK CRUDE OIL STRG 3800-TK-048
Tickalara Satellite | Trunkline | Tickalara Satellite - Crude Oil Storage | Production Tanks | 3800-SAT-STO-PRO | 3800-SAT-STO-PRO | Tickalara Satellite - Crude Oil Storage - Production Tanks | KICK CRUDE OIL STRG | KICK CRUDE OIL STRG 3800-SAT-STO-PRO
Tickalara Satellite | Trunkline | Tickalara Satellite - Trunkline | Control and Monitor | 3800-TK-054-CO | 3800-TK-054-CO | Tickalara Satellite - Trunkline - Control and Monitor | KICK TRNKLN | KICK TRNKLN 3800-TK-054-CO
Tickalara Satellite | Trunkline | Tickalara Satellite - Trunkline | Control and Monitor | 3800-PSV-0015 | 3800-PSV-0015 | Tickalara Satellite - Trunkline - Control and Monitor | KICK TRNKLN | KICK TRNKLN 3800-PSV-0015
Tickalara Satellite | Trunkline | Tickalara Satellite - Trunkline | Control and Monitor | 3800-TL-WAT-CO | 3800-TL-WAT-CO | Tickalara Satellite - Trunkline - Control and Monitor | KICK TRNKLN | KICK TRNKLN 3800-TL-WAT-CO